## Pre Bid Clarifications
Declaration : The compiled Pre Bid Queries have been reproduced on as it is basis, without any modifications.
Tender No. SECI/C&P/OP/17/007/2022-23 Dated: 15/03/2023
The Design, Engineering, Supply, Construction, Erection, Testing & Commissioning of 100 MW (AC) Floating Solar PV Project having 10 years plant O&M At Getalsud Dam, Ranchi, Jharkhand India
Sl. No. | Tender Section | Page No. | Clause | Description as per Bidding Document | Queries | Category | Clarifications
1 | APPENDIX – A TO SECTION – VII | 5 of 309 | 1 | Origin of Cell / Module Manufacturer: Open | Being world Bank funded project, we understand that there is no restriction for the procurement from land border sharing countries with India. Kindly clarify. | Technical-Electrical | No, there is no restriction for procurement from land Border sharing countries.
2 | APPENDIX – A TO SECTION – VII | 5 of 309 | 1 | Owner of Water Body & Land: Water Resource Department, Jharkhand | We understand that the water body and land shall be handed over by SECI to contractor. Kindly confirm. | Contractual | Yes
3 | APPENDIX – A TO SECTION – VII | 5 of 309 | 1 | Bay -111 & Bay-112 of 132/33 kV IRBA GSS (JUSNL) Short Circuit Levels: 132 kV Bus: 31.5 kA/s 33 kV Bus: 25 kA/3 sec 132 kV Switching Scheme - Double Bus Single Breaker Scheme | It is requested to kindly share the route map for the transmission line. | Technical-Electrical | Please refer Annexure L - Tentative Route Map for Transmission Line (S. No. of Amendment 1)
| APPENDIX – A TO SECTION – VII | 6 of 309 | 1 | Transmission Line from Plant till Interconnection Point: 132 kV Double Circuit with ACSR ZEBRA Conductor
4 | APPENDIX – A TO SECTION – VII | 6 of 309 | 1 | Construction Water: To be arranged by the Contractor | Please confirm whether the Reservoir water can be used for the construction purpose. | Projects | Reservoir Water can be taken subject to payment of applicable rates by the contractor to WRD Jharkhand (rates available on Website)
5 | APPENDIX – A TO SECTION – VII | 6 of 309 | 1 | Construction Power: To be arranged by the Contractor | It is requested to consider that the power required during construction to be arranged by SECI. | Projects | SECI may facilitate EPC agency in getting power connection but the charges against the units consumed will have to be borne by the contractor
6 | APPENDIX – A TO SECTION – VII | 8 of 309 | Clause 2, Sl No. 18 | Statutory approvals required for setting up of the project. 1. Consent from the JUSNL /JBVNL for the evacuation of the power generated by Floating Solar Grid Interactive Floating Solar Power Projects. 2. Consent to establish the project during construction and consent to operate the project after the commissioning of the plant from Jharkhand Pollution Control Board (JPCB) 3. Approval of the Electrical Inspectorate, Government of Jharkhand for commissioning of the transmission line and the Floating Solar power project installed at the Project Site. 4. Certificate of Commissioning of the Floating Solar Grid Interactive Power Project issued by JBVNL. 5. SNA/JREDA registration certificate, if required. 6. Permission from all other statutory and nonstatutory bodies required for the Project. 7. Clearance from Department of Forest, Ecology and Environment, if required. | Being SECI Owner/Employer of the project, it is requested to kindly consider the statutory approvals in the scope of SECI. However, contractor will provide the necessary support for obtaining the approvals. On placing of order to successful Bidder, SECI should have obtained all necessary approvals to establish the project. CEIG approval shall be taken by contractor. | Projects | The terms and conditions of the RfB shall prevail.
7 | APPENDIX – A TO SECTION – VII | 8 of 309 | Clause 2, Sl No. 19 | Water body approvals, agreement and charges, if any: Consent/ Approval shall be sought from Water Resources Department, GoJ before construction | Being SECI Owner/Employer of the project, the consent/Approval from Water Resource Department, GoJ shall be taken by SECI. Kindly confirm. | Projects | The terms and conditions of the RfB shall prevail.
8 | APPENDIX – A TO SECTION – VII | 17 of 309 | 7.1 | Obtaining statutory approvals /clearances/ compliances on behalf of the Employer from various Government Departments, not limited to, the following: -  Pollution control board clearance, if required  Mining Department, if required  Forest Department, if required  All other approvals as and when, as necessary for setting up of a solar power plant including CEIG/ CEA, connectivity, power evacuation, Railways, Port Trust authorities etc. (as applicable) as per the suggested guidelines. | Being SECI Owner/Employer of the project, it is requested to kindly consider the statutory approvals/clearances in the scope of SECI . However, contractor will provide the necessary support for obtaining the approvals. CEIG approval shall be taken by contractor. | Projects | The terms and conditions of the RfB shall prevail.
9 | APPENDIX – A TO SECTION – VII | 18 of 309 | 7.1.1 | All statutory approvals/permissions and/or No Objection Certificates (NoC) etc. from the DISCOM for obtaining connectivity at the substation as per Project Particulars provided above. | Being SECI Owner/Employer of the project, all statutory approvals/permissions and/or No objection certificate from DISCOM shall be arranged by SECI. Kinldy confirm. | Projects | The terms and conditions of the RfB shall prevail.
10 | APPENDIX – A TO SECTION – VII | 18 of 309 | 7.1.2 | All other statutory approvals and permissions and their respective compliances, not mentioned specifically but are required to carry out hassle free Construction and O&M of the plant. | Being SECI Owner/Employer of the project, It is requested to kindly consider that all the statutory approvals except CEIG shall be in the scope of SECI. Kindly consider. | Projects | The terms and conditions of the RfB shall prevail.
11 | APPENDIX – A TO SECTION – VII | 32 of 309 | 1.3 | The PV Modules Supplier should have supplied minimum 5 GW capacity globally or 500 MW in India in the past 5 years as on last date of bid submission. | kindly wave off this requirement as this will restrict the Module suppliers. | Technical-Electrical | The terms and conditions of the RfB shall prevail.
12 | APPENDIX – A TO SECTION – VII | 133 of 309 | 31.2 | The Contractor shall get the route approval from the EMPLOYER and STU prior to start of the construction. Any changes in the route or scheme at any point of the time prior to commissioning shall be complied without any additional cost to the EMPLOYER. | Route approval may be provided by SECI to bidders in order to firm up the transmission line estimate. | Projects | Bidders may choose the route most feasible to them for obtaining the clearances within the stipulated time limits.
13 | APPENDIX – A TO SECTION – VII | 133 of 309 | 31.3 | The ROW for the TL/UG cable shall be obtained prior to the construction of the line from the concerned authorities. | It is requested to either kindly consider the scope of ROW in the scope of Employer or completely exclude the scope of transmission line from the scope of contractor. Kindly accept and confirm. This is requested to ensure timely commissioning of the solar project | Projects | Not Acceptable. However SECI/ JBVNL will facilitate the contractor in obtaining the clearances.
14 | APPENDIX – A TO SECTION – VII | 168 of 309 | Cl. No. 3. Specific Requirements; Sl. No. 2 | Maximum block size for the FSPV plant shall not be higher than 4 MW (AC). Blocks shall be symmetrical in shape. | Restricting block size may lead to increase of anchoring & mooring cost. Please review and allow the best possible block size as per design criteria. The block sizes shall anyway be simulated in CFD and the designed block size shall be arrived based on boundary conditions. | Technical-Civil | Please refer Amendment 01
15 | APPENDIX – A TO SECTION – VII | 168 of 309 | Cl. No. 3. Specific Requirements; Sl. No. 1 | Angle of tilt for the PV array shall not exceed 5°. | It is requested to not to restrict the tilt angle as 5° and kindly consider that the tilt angle shall be finalized during detail engineering. Kindly consider. | Technical-Electrical | The terms and conditions of the RfB shall prevail.
16 | ANNEXURE 1: Scope of Work for Operation and Maintenance | 268 of 309 | xxxii | Water requirement for module cleaning arrangement and the cost for the same shall be borne by Contractor. The Contractor shall arrange for water on it’s own, by ensuring ESIA norms. | It is requested to kindly consider the water charges during O&M in the scope of Employer. | Projects | The terms and conditions of the RfB shall prevail.
17 | Section II - Bid Data Sheet | 56 of 365 | 17.5.2 | The Project through International Competitive Bidding & funded by World Bank shall be treated as Deemed Export and therefore the Basic Custom Duty (BCD) is exempted on the imported supply of the goods against “Project Authority Certificate (PAC)”. Bidders who have considered Deemed Export benefit while submitting their bids, shall be responsible to claim refund of BCD from the Govt, for which employer shall furnish necessary PAC, details and undertaking that such supplies are getting imported for the use & execution of the said project. Further, the necessary documents / certificates as may be required to claim the BCD exemption shall be provided by the Employer to the Supplier. | We understand these exemptions are applicable on transactions other than direct transactions between contractor & SECI. | Contractual | Query not clear. However the understanding may be gathered regarding the deemed export benefit is that there is no BCD applicable for WB funded projects against the PAC provided by Owner. In such situations such exemptions are availed at the customs level only and the applicable BCD amount mentioned under the SOR 1 is not invoiced/billed to the Owner, as the benefit of the BCD has already been claimed at the Custom level.
18 | Bid Data Sheet | 61 OF 365 | 42.1 | “BAFO applies. Please see sub-section 1.2, Para D. Procedure for Best and Final Offer, Section III for further details. There will be no negotiation after the BAFO | It is understood that there is no reverse auction in this tender and all the technically qualified bidders are permitted to participate in the BAFO. Kindly Confirm. | Contractual | Yes there will be no reverse auction in this tender. However, bidders will be given one more chance to revise their bid post Financial Evaluation in the form of BAFO.
| Evaluation Criteria | 65 OF 365 | 1.2 (A) | The evaluation of the price bids will be conducted in the below mentioned manner, which will be followed by BAFO:
19 | Standard Procurement Document | 6 of 365 | 7 | All Bids must be accompanied by a Bid Security of the INR 6 Crores (Indian Rupees Six Crores only), or USD 1 Mn (US Dollars One Million only) as specified for the contract in case of a Bid Security | It is requested to kindly consider the Bid Security Declaration instead of Bid Security. BHEL being central PSU may kindly be permitted for Bid Security Declaration. Kindly consider. | Contractual | The terms and conditions of the RfB shall prevail.
| Bid Data Sheet | 57 of 365 | 20.1 | A Bid Security shall be required. A Bid-Securing Declaration shall not be required. The amount and currency of the Bid Security shall be 6 Cr (Indian Rupees Six Crores only) or USD 1 Mn (US Dollars One Million only)
20 | Bid Data Sheet | 57 of 365 | 19.1 | The Bid shall be valid for 180 days after the Bid submission/Extended Bid submission deadline. | In view of the high volatility in prices in Solar segment, OEMs are not giving the long term price validity, hence it is requested to kindly consider the bid validity as 90 days. | Contractual | The terms and conditions of the RfB shall prevail.
21 | Evaluation Criteria | 65 of 365 | 1 (C) | Evaluated Bid Value (EBV) | For evaluation of bid, it is requested to kindly include taxes & duties. The bidder who intends to import the item(s)/equipment(s) will have the advantage over the bidder who intends to supply the indigenous item(s)/equipment(s) as the duties will not be considered for evaluation of bid. | Contractual | The terms and conditions of the RfB shall prevail.
22 | Evaluation Criteria | 66 of 365 | 1 | Employer will pay the amount for BCD+SWS & SGD/ADD against the submission of documentary evidence with a MAXIMUM CEILING of BCD+SWS & SGD/ADD charges as mentioned by the Bidder in the Price Schedules No 1 at the time of bidding. Bidders are required to quote the applicable BCD+SWS & SGD/ADD with due diligence & appropriate financial prudence, as afterwards bidders will not be able to change or claim such taxes & duties already quoted during the bid. The ceiling amount of BCD+SWS & SGD/ADD is applicable only for the purpose of Award, however, any change in such taxes and duties or introduction of new law during the entire course of the contract, will be treated in line with the "Change in Law & Regulations" GCC clause 36 of the RfB. No BCD+SWS & SGD/ADD will be reimbursed to the contractor in the absence of documentary proofs. | It is requested to kindly re-imburse BCD+SWS & SGD/ADD at actuals without ceiling in line with the GCC Clause No. 36.1 regarding Change in Law. | Contractual | The terms and conditions of the RfB shall prevail.
23 | Evaluation Criteria | 66 of 365 | 1 | The payment of GST by the Employer shall only be at the CEILING of GST as mentioned by the Bidder in the Schedule No 1 at the time of bidding. Bidders are required to quote the applicable GST with due diligence & appropriate financial prudence, as afterwards bidders will not be able to change or claim the GST charges already quoted during the bid. | It is requested to kindly re-imburse the GST at actuals under the change in law clause without the ceiling limit. Further this is in contrary to the GCC Clause No. 36.1 regarding Change in Law. | Contractual | The change in law is only applicable in case any such Change in Law event happens as detailed under GCC Clause No. 36.1. However the ceiling amount is for the quoted GST amount which is being diligently mentioned by the bidder in the SOR Sheet. However in the event of any such Change in law, the treatment will be done accordingly as mentioned under the GCC Clause No. 36.1 of RfB.
24 | Evaluation Criteria | 67 of 365 | 2 | The payment of GST by the Employer shall only be at the CEILING of GST as mentioned by the Bidder in the Schedule No 2 at the time of bidding. Bidders are required to quote the applicable GST with due diligence & appropriate financial prudence, as afterwards bidders will not be able to change or claim the GST charges already quoted during the bid. | It is requested to kindly re-imburse the GST at actuals under the change in law clause without the ceiling limit. Further this is in contrary to the GCC Clause No. 36.1 regarding Change in Law. | Contractual | The change in law is only applicable in case any such Change in Law event happens as detailed under GCC Clause No. 36.1. However the ceiling amount is for the quoted GST amount which is being diligently mentioned by the bidder in the SOR Sheet. However in the event of any such Change in law, the treatment will be done accordingly as mentioned under the GCC Clause No. 36.1 of RfB.
25 | Evaluation Criteria | 67 of 365 | 3 | The payment of GST/Taxation by the Employer shall only be at the CEILING of GST/Taxation as mentioned by the Bidder in the Schedule No 3 at the time of bidding. Bidders are required to quote the applicable GST/Taxation with due diligence & appropriate financial prudence, as afterwards bidders will not be able to change or claim the GST charges already quoted during the bid. | It is requested to kindly re-imburse the GST at actuals under the change in law clause without the ceiling limit. Further this is in contrary to the GCC Clause No. 36.1 regarding Change in Law. | Contractual | The change in law is only applicable in case any such Change in Law event happens as detailed under GCC Clause No. 36.1. However the ceiling amount is for the quoted GST amount which is being diligently mentioned by the bidder in the SOR Sheet. However in the event of any such Change in law, the treatment will be done accordingly as mentioned under the GCC Clause No. 36.1 of RfB.
26 | Evaluation Criteria | 67 of 365 | 4 | The payment of GST/Taxation by the Employer shall only be at the CEILING of GST/Taxation as mentioned by the Bidder in the Schedule No 4 at the time of bidding. Bidders are required to quote the applicable GST/Taxation with due diligence & appropriate financial prudence, as afterwards bidders will not be able to change or claim the GST charges already quoted during the bid. | It is requested to kindly re-imburse the GST at actuals under the change in law clause without the ceiling limit. Further this is in contrary to the GCC Clause No. 36.1 regarding Change in Law. | Contractual | The change in law is only applicable in case any such Change in Law event happens as detailed under GCC Clause No. 36.1. However the ceiling amount is for the quoted GST amount which is being diligently mentioned by the bidder in the SOR Sheet. However in the event of any such Change in law, the treatment will be done accordingly as mentioned under the GCC Clause No. 36.1 of RfB.
27 | Evaluation Criteria | 68 of 365 | 5 | The payment of GST by the Employer shall only be at the CEILING of GST as mentioned by the Bidder in the Schedule No 5 at the time of bidding. Bidders are required to quote the applicable GST/Taxation with due diligence & appropriate financial prudence, as afterwards bidders will not be able to change or claim the GST charges already quoted during the bid. | It is requested to kindly re-imburse the GST at actuals under the change in law clause without the ceiling limit. Further this is in contrary to the GCC Clause No. 36.1 regarding Change in Law. | Contractual | The change in law is only applicable in case any such Change in Law event happens as detailed under GCC Clause No. 36.1. However the ceiling amount is for the quoted GST amount which is being diligently mentioned by the bidder in the SOR Sheet. However in the event of any such Change in law, the treatment will be done accordingly as mentioned under the GCC Clause No. 36.1 of RfB.
28 | PCC | 319 of 365 | 8.2 | The Time for Completion of the whole of the Plant Facilities shall be 18 (Eighteen) Months till commissioning from the Effective Date as described in the Contract Agreement or NTP, whichever is later. | Considering the size of Solar floating project and transmission line it is requested to kindly consider the time for commissioning as at least 24 months from the handing over of site. Kindly accept. | Contractual | Considering the floating solar project the timeline has already been kept on higher side of 18 months when compared to timeline given for ground mounted solar PV (12 months).
29 | PCC | 318 of 365 | 1 | Effective Date: “Effective Date” of the Contract will be starting from the date as mentioned in the Contract Agreement or Notice to Proceed (NTP) provided by the Employer, whichever is later. NTP will be provided by the employer in the shortest possible time and all contractual obligations will be started from the date of Contract Agreement (CA) or Notice to Proceed, whichever is later. | It is requested to kindly consider the effective date as the date of handing over of encumbrance free water body and land. Kindly accept. | Contractual | The terms and conditions of the RfB shall prevail.
30 | General |  |  | Monthly Reference Radiation | It is requested to kindly share the reference radiation which to be considered by bidders. | Technical-Electrical | Yearly reference radiation has been shared in Annexure-G which shall be used to calculate the radiation correction factor during CUF calculations.
31 | Standard Procurement Document | 163 of 365 |  | Country of Origin Declaration Form | As at the stage of bidding, the country of origin can not be finalized. Hence, it is requested to kindly consider to accept the details at later stage. | Contractual | The tentative list of country of origin may be provided.
32 | Standard Procurement Document | 164 of 365 |  | Declaration regarding Imported items | As at the stage of bidding, import content can not be finalized. Hence, it is requested to kindly consider to accept the details at later stage. | Contractual | For claiming the deemed export benefit the declaration of import content is mandatory during the bidding stage as it is a vital component of documentation at customs during the production of PAC. Bidders are requested to consider this amount with due diligence considering contingency/change in sourcing basket/county of origin and provide the mandatory details of import contents on the SOR1 sheet.
33 | GCC | 268 of 365 | 37 | Force Majeure | It is requested to kindly consider the Pandemic, epidemic, Lockdown etc as Force Majeure. Kindly accept. | Contractual | Please refer to GCC Clause 37.1 (d) wherein epidemic and quarantine are duly covered under Force Majeure. However any special circumstances may be dealt on case to case basis.
34 | GCC | 287 of365 | 46 | Disputes and Arbitration | As per the Office Memorandum (OM) dated 22.05.2018 of Ministry of Heavy Industries & Public Enterprises (S.No. 4(1)/2013-DPE(GM)/FTS-1835), which has been marked to Chief Secretary of all states, whereby disputes or differences between Central Public Sector Enterprise (CPSE) and state government Department/ Organization relating to the interpretation and application of the provisions of commercial contract(s), shall be taken up for resolution through AMRCD. Kindly confirm. | Contractual | The terms and conditions of the RfB shall prevail.
35 | PCC: Employer’s Responsibility | 321 of365 | 10.3 | The Employer shall facilitate the contractor in acquiring and obtaining for all permits, approvals and/or licenses from all local, state or national government authorities or public service undertakings in the country where the Site is located which (a) such authorities or undertakings are to obtain in the Employer’s name, (b) are necessary for the execution of the Contract, including those required for the performance by both the Contractor and the Employer of their respective obligations under the Contract, and (c) are specified in the Appendix (Scope of Works and Supply by the Employer). The related payments/fees of obtaining permits, approvals and/or licenses from all local, state or national government authorities or public service undertakings in the country where the Site is located will be in the contractor scope. | Except CEIG approval, It is requested to kindly consider that the all approvals, permits, licenses shall be in the scope of Employer. However, contractor shall support Employer while obtaining the approvals. Kindly accept. | Contractual | Obtaining statutory approval will be in the scope of the Contractor. However JBVNL/WRD Jharkhand will provide support at every stage to the Contractor in case of any difficulties faced by Contractor in obtaining such statutory approval.
36 | PCC | 322 of 365 | 13 | Second Stage: The value of the Contract Performance Security shall be 5% (Five) of the Contract Value {i.e. total sum of the Supply (Abroad & Employer’s country) & Service (Freight, Design, Installation & Civil Works) starting from the Operational Acceptance of the Plant Facilities, valid till the end of 10th year of the O&M period. | It is requested to kindly consider that the Performance security during O&M as 5 % of O&M contract Price instead of EPC Price. Kindly accept. | Contractual | The terms and conditions of the RfB shall prevail.
37 | Appendix 1. Terms and Procedures of Payment | 341 of 365 |  | Seventy percent (70%) of the total or pro rata amount (of Schedule No. 1), upon delivery to the destination within forty-five (45) days after receipt of materials and relevant documents | It is requested to kindly consider the following to avoid negative cash flow of contractor. i. 55% payment on dispatch through Letter of Credit payable at Sight. Ii. 25% on receipt of material at site iii. 5% on commissioning iv. 5% on final acceptance test | Contractual | The terms and conditions of the RfB shall prevail.
| Appendix 1. Terms and Procedures of Payment | 341 of 365 |  | Ten percent (10%) of the total or pro rata amount (of Schedule No. 1), upon successful erection, testing and commissioning of materials at site and Operational Acceptance of the plant pursuant to successful functional Guarantee Tests.
| Appendix 1. Terms and Procedures of Payment | 341 of 365 |  | Ten percent (10 %) of the total or pro rata amount (of Schedule No. 1) within forty-five (45) days of receipt of invoice after final acceptance of the Plant facilities, pursuant to submission of all requisite documentation including submission of all as-built drawings and documents..
38 | Appendix 1. Terms and Procedures of Payment |  |  | Release of Payment | It is requested to kindly consider to release the payment maximum within 30 days of submission of invoices. | Contractual | The terms and conditions of the RfB shall prevail.
39 | Appendix 1. Terms and Procedures of Payment | 344 of 365 | g | All payments to be made directly to the Contractor shall be made by the Employer though electronic payment mechanism (e-payment) for which necessary details shall be tied up during execution of the Contract. However, a request for payment to be released through cheque shall be considered on case to case basis and merit of the same. | It is requested to kindly consider the release of payment through irrevocable Letter of Credit payable at sight. | Contractual | The terms and conditions of the RfB shall prevail.
40 | SECTION – VII; CHAPTER-1; SCOPE OF WORK | 8 of 309 | Cl. No. 2; Sl. No. 17 | Maximum velocity value shall be considered after performing flood routing studies using software simulations or hydraulic model study to derive flow path and critical velocities. Additionally, water current velocity shall be measured at upstream and downstream of proposed site for at least 30 days using suitable Acoustic Doppler Current Profiler (ADCP)/Current Meter. The velocity measurements should be undertaken at surface, at half of the water depth, and at 0.5 m above the reservoir bed. | As the velocity measurements are a critical input for the design of the FSPV system, hence BHEL requests SECI to conduct this study and provide a standard value to all its bidders. Also the location of the project site is the upstream of the dam, hence the requirement of velocity studies at the downstream of the dam is not understood. | Technical-Civil | Velocity measurements are under the scope of the Contractor. Terms and conditions in the tender document shall prevail.
41 | SECTION – VII; CHAPTER-1; SCOPE OF WORK | 9 of 309 | 3.2 | All documents and drawings (soft copy) shall be submitted to the Employer for review and approval. Every drawing shall also be submitted in ‘*.dwg’ format. In case of design calculations done in spread sheet, editable (working) soft copy of the spread sheet shall also be submitted along with ‘pdf’ copies during every submission. | The submission of drawing in hard copies before approval in cat-I is to be reviewed. All soft copies of the documents and drawings shall be uploaded on an online platform for the seamless review of customer. Also there can be multiple revisions for approval. The final approved set of drawings shall be submitted in hard copy. | Technical-Electrical | Agreed.
42 | TECHNICAL SPECIFICATIONS | 156 of 309 | 28.2.1 | Re. Density > 0.9 Compressive Stress at Yield > 6 MPa More than 50% of its original break elongation after 3,000 hours exposure | The requirement given for HDPE is much higher than the current Industry practices used for Floating solar platforms. This will increase the cost of HDPE floating platforms. May kindly review the required values as per current market availability: Re. Density - 0.90-0.96 (g/cc) Compressive Stress at Yield- not required Elongation at yield> 8 % | Technical-Civil | The terms and conditions of the RfB shall prevail.
43 | TECHNICAL SPECIFICATIONS | 157 of 309 | 28.2.1 | UL 94 or Equivalent IEC/ISO standard: Standard for Safety of Flammability of Plastic Materials for Parts in Devices and Appliances testing | This standard is not available readily. Please provide. | Technical-Electrical | These are proprietary Standards which cannot be shared.
44 | TECHNICAL SPECIFICATIONS | 157 of 309 | 28.2.2 | For design of anchoring and mooring system, the following standards may referred (for guidance) – API RP 2SK, API Spec 2F, API RP 2I, API RP 2MIM, BS 6349-6 | Please add API RP 2A for floater strength verification, spreader bar design & pad eye design. Also DNV-RP-C205 for environmental loads shall be added. | Technical-Civil | The mentioned standards have already been specified in the tender document.
45 | TECHNICAL SPECIFICATIONS | 157 of 309 | 28.4 | The floating system shall consist of multiple modular floating units/platforms and connected to the ground using anchoring and mooring system. However, the float unit shall have average material thickness of 3 mm (minimum material thickness of 2.5 mm), with moisture retention of less than 5%. Floating system/platform shall be fenced with vacant floats to demarcate boundary. | Achieving minimum thickness of 3 mm will increase the cost of manufacturing of Floaters which is uneconomical. Also the complete design of floaters with spreader bars and mooring system will be simulated and wherever higher thickness of floaters is required shall be provided. Request to keep it average thickness of 3 mm. All side walkway/ cable route floats will be there to demarcate the block; hence additional vacant floater will increase the costing. | Technical-Civil | The Clause specifies average material thickness of 3mm and minimum material thickness of 2.5mm. The terms and conditions in the tender document shall prevail.
46 | TECHNICAL SPECIFICATIONS | 159 of 309 | 28.22.1 | The floating platform shall be made of HDPE/FRP or precast or cast in-situ fixed platform and shall be of adequate size for installation of equipment, associated facilities, movement and working of O&M personnel, etc. | BHEL proposes following material for construction of Inverter platforms in water: Mild steel/Stainless Steel/HDPE/FRP/ precast or cast in-situ fixed platform/ RCC/Ferro cement. | Technical-Civil | Please refer Amendment 01.
47 |  |  |  | General Query | Please provide KML file to know the exact location and boundary of the usable FSPV area. | Projects | .dwg file is attached as per annexure-K. Please refer amendments.
48 |  |  |  | General Query | Please confirm the availability of land on the bank of reservoir for following requirement of Installation of FSPVs: - Area for control room construction -Area for storage of Module, Floaters, construction material etc. -Area for working of different contractors at site. - Floater Assembly area and Launching Platform area As per BHEL Experience, minimum 25 Acres of area is required. | Contractual | Identification, Demarcation, Boundary and necessary Infra Developments for the usage of such land is under the scope of Contractor. Owner along with the state authority will facilitate all possible support in obtaining the same.
49 |  |  |  | General Query | Please define the indicative MQP for floaters. | Technical-Civil | MQP for floats will be finalized during detail engineering as per the approved design and equipment.
50 | TECHNICAL SPECIFICATIONS | 16 of 309 | 6.6 | General clearing of plant site and TL corridor by cutting of any vegetation & shrubs including disposal of waste material. | It is understood that TL corridor from Plant Substation to Interconnection point is under EPC vendor scope. Kindly confirm. | Projects | Yes
51 | TECHNICAL SPECIFICATIONS | 17 of 309 | 6.15 | Construction of floating fence around off-shore portion of the plant. | It is not possible for movement of boat or equipment platform movement (in case of emergency) if the array closes with floating fencing and the entry /exit points will be restricted which will affect the movement space. Kindly reconsider to remove the scope of floating fencing for arrays. | Technical-Electrical | The terms and conditions of the RfB shall prevail.
52 | TECHNICAL SPECIFICATIONS | 17 of 309 | 6.19 | Construction of water tanks, plumbing network for drinking water and cleaning of PV Modules. | Water from the reservoir will be used for cleaning the PV modules, hence construction of water tanks for cleaning of PV modules is not required. Kindly confirm. | Technical-Electrical | Please refer detailed Clause for PV Module Cleaning System. The terms and conditions of the RfB shall prevail.
53 | TECHNICAL SPECIFICATIONS | 142 of 309 | 7.2 | The Approach road connecting nearest public road and the Main gate shall be of 4.0m wide carriage way with 0.5m wide shoulders on either side. | What is the approx.. length of approach road connecting nearest public road and the Main gate | Projects | Substation land is situated on public road
54 | TECHNICAL SPECIFICATIONS | 145 of 309 | 9.8.1 | Floating fence with floating buoys (with durable UV resistant material suitable to withstand the aqueous environment, be eco-friendly to bio diversity, and withstand pressure of debris/trees/flotsam through river during monsoon period) shall be formed around every floating platform. | Kindly reconsider to remove the scope of floating fencing for arrays | Technical-Civil | The terms and conditions of the RfB shall prevail.
55 | TECHNICAL SPECIFICATIONS | 152 of 309 | 24.8 | The external buried cables shall be laid in excavated trench as specified under specifications for Electrical works. The sand for filling shall be of Grade – IV conforming to IS: 383. | As per IS 1255, cl no: 8.7 A bedding of riddled earth or river sand should be provided and protective cable warning covers should be used. As Grade-IV sand will not be available in open market, kindly allow as per IS 1255 for buried cables. | Technical-Civil | The terms and conditions of the RfB shall prevail.
56 | TECHNICAL SPECIFICATIONS | 155 of 309 | 26.8 | Module washing tank: The Polyethylene storage tank shall conform to IS 12701 | Tank will not be required if the water pumping to be done directly from reservoir. Kindly confirm. | Technical-Civil | The terms and conditions of the RfB shall prevail.
57 | TECHNICAL SPECIFICATIONS | 158 of 309 | 28.11 | All fasteners used in the floating system shall be made of SS 316. | Kindly reconsider if HDPE connector are used | Technical-Civil | Please refer S. No. of Amendment 3.
58 | TECHNICAL SPECIFICATIONS | 6 of 309 |  | Performance Ratio (PR) at 132 kV side of Plant Substation - 84.4% | Please limit the PR Value to 81%- Please confirm | Technical-Electrical | The terms and conditions of the RfB shall prevail.
59 | CHAPTER 1: SCOPE OF WORK/ TECHNICAL SPECIFICATIONS | 8 of 309 | Cl. No. 2; Sl. No. 17 | Maximum velocity value shall be considered after performing flood routing studies using software simulations or hydraulic model study to derive flow path and critical velocities. Additionally, water current velocity shall be measured at upstream and downstream of proposed site for at least 30 days using suitable Acoustic Doppler Current Profiler (ADCP) /Current Meter. The velocity measurements should be undertaken at surface, at half of the water depth, and at 0.5 m above the reservoir bed. | As the velocity measurements are a critical input for the design of the FSPV system, hence BHEL requests SECI to conduct this study and provide a standard value to all its bidders. Also the location of the project site is the upstream of the dam, hence the requirement of velocity studies at the downstream of the dam is not understood. | Technical-Civil | The terms and conditions of the RfB shall prevail.
60 | TECHNICAL SPECIFICATIONS | 9 of 309 | 3.2 | All documents and drawings (soft copy) shall be submitted to the Employer for review and approval. Every drawing shall also be submitted in ‘*.dwg’ format. In case of design calculations done in spread sheet, editable (working) soft copy of the spread sheet shall also be submitted along with ‘pdf’ copies during every submission. | The submission of drawing in hard copies before approval in cat-I is to be reviewed. All soft copies of the documents and drawings shall be uploaded on an online platform for the seamless review of customer. Also there can be multiple revisions for approval. The final approved set of drawings shall be submitted in hard copy. | Technical-Electrical | Agreed.
61 | TECHNICAL SPECIFICATIONS | 155 of 309 | 26.7 | The Contractor shall propose a suitable module cleaning system which shall include installation of ground mounted/offshore polyethylene tank(s) of required storage capacity, pumps (including 1 No. standby pump), water supply mains and flexible hose pipes, taps, valves (NRV, Butterfly valve, Ball valve, Gate valve, PRV, scour valve etc.), Water hammer arrester(s), pressure gauge, flow meter etc. as per the planning & design. | Laying pipe network is quite difficult in FSPVs. BHEL Proposes Module washing system shall be done with hand held portable Pressure pump for drawing water from below the floater and providing water jet to clean the PV modules. Pump motor shall be operated with either diesel/Petrol/Battery. The pump set shall be complete with nozzle and flexible hose of 15 m length with a sprayer. The pump shall be capable of providing water jet of required pressure to clean the PV modules in two adjacent rows at a time. Being portable pump, after completing cleaning in two row, the pump will be shifted for cleaning of other rows through walkway. The water of the dam shall be used for module cleaning. | Technical-Civil | The terms and conditions of the RfB shall prevail.
62 | General |  |  |  | Applicable taxes & duties on contract cancellation charges shall be on account of employer. | Contractual | The terms and conditions of the RfB shall prevail.
63 | General |  |  |  | Liquidated Damages/Penalty shall not be imposed on contractor, if the delay is attributable to SECI. | Contractual | All such special circumstances may be dealt on case to case basis & all potential delays and associated additional costs that are attributable to the Employer shall be dealt with according to the contract.
64 | General |  |  |  | We request SECI to kindly consider the price and time implication due to change in law, regulation, ordinance, order as the Contractor will be bound to adhere any the change in law, regulation, ordinances and orders issued by government. | Contractual | All such special circumstances may be dealt on case to case basis & all potential delays and associated additional costs that are attributable to the Employer shall be dealt with according to the contract.
65 | General |  |  |  | If delay from scheduled completion is on account of employer, then any statutory variation beyond stipulated Delivery/ Commissioning/Completion schedule shall be to customer’s account. | Contractual | All such special circumstances may be dealt on case to case basis & all potential delays and associated additional costs that are attributable to the Employer shall be dealt with according to the contract.
66 | General |  |  |  | It is requested to kindly consider that no Liquidated Damages/Penalty shall be imposed on account of delay due to Force Majeure. | Contractual | The terms and conditions of the RfB shall prevail.
67 | General |  |  |  | The delay in commissioning/completion due to external issues beyond the control of contractor shall not be in the account of Contractor. As per the site visit it is gathered that the reservoir is used for fishing purpose by locals which may cause hinderance during the execution of the project. In case of delay due to the local disturbance will not be in the account of contractor. Kindly accept and confirm. | Contractual | The terms and conditions of the RfB shall prevail.
68 | General |  |  |  | Sufficient area (~ 25 acres) required for storage and assembly of floater/equipment to be arranged by SECI. Kindly accept and confirm. | Projects | EPC agency has to arrange the same by themselves as per their requirement and the rent applicable has to be borne by them.
69 | General |  |  |  | We request to propose a date for joint Site visit | Contractual | The site visit has already been conducted.
70 | General |  |  |  | As this tender is being financed by World Bank, we understand that the General Financial Rules (GFRs), 2017 regarding restriction of global tender enquiry for the tenders up to Rs 200 Cr or such limit as may be prescribed by the Department of Expenditure from time to time shall not be applicable in this tender and the required approvals for relaxation shall be provided by SECI. | Contractual | This being a World funded project, the World Bank Procurement regulations applies as per World Bank’s “Procurement Regulations for IPF Borrowers- Procurement in Investment Projects Financing”, July 2016 revised 1 November 2017 and August 2018 (“Procurement Regulations”)
71 | Appendix - A to Section VII: TECHNICAL SPECIFICATIONS | 213 of 309 | Annexure-C (PG Test Procedure) | Liquidated Damages for Shortfall in PR: For every 0.01 shortfall in PR below the committed PR value, a penalty of 1% of the total Contract Value (i.e., total sum of all the Supply and Service) shall be levied. In case the Contract Performance Security has already been encashed on account of any default/delays, the penalty amount will be recovered from any due payments to the contractor. In case the Plant PR Shortfall is more than 0.05 than the specified PR value, then the total plant will be accepted on as-is basis & the total Contract Performance Security submitted by the contractor will be forfeited & payments linked to operational acceptance will not be made. | These three (03) penalties are indicated which are linked to Performance of the Plant. However, there should be only one (01) penalty for the performance of the plant. Penalty for failing to achieve the annual guaranteed CUF at the end of 10th year (as indicated on page number 355-356 of 365 of the file named Standard Procurement Document) to be deleted as the Contractor will have the O&M only up to 10 year. For the remaining two penalties mentioned at page 202 of 309 of file named Standard Procurement Document and page number 44 of 50 of appendix-B to be considered as there should be only one penalty linked to the performance of the plant. | Technical-Electrical | Liquidated Damages for Shortfall in PR as per Annexure C (PG Test Procedure) are applicable for Operational Acceptance of the Plant, where Contract Value refers to the Sum of the Supply and Services of the EPC Contract. Liquidated Damages for Shortfall in CUF shall be as per the Annexure 2 to the Annexure G: Operation & Maintenance Agreement of 100 MW (AC) Floating Solar PV Project at Getalsud Dam, Ranchi. 2 (D) (ii), Appendix 8. Functional Guarantees is Amended accordingly. Please refer Amendment 1.
| Standard Procurement Document | 355-356 of 365 | 2 (D) (ii), Appendix 8. Functional Guarantees | If the Contractor fails to achieve the annual guaranteed CUF at the end of 10th year, then the Contractor shall pay compensation to the Employer an amount equal to the Net Present Value (NPV) of the revenue loss for 10th to 25th year calculated as below: (a) % CUF drop i.e. [(Guaranteed CUF of 10th year – Actual CUF of 10th year) / Guaranteed CUF of 10th year]*100 in the 10th year shall be considered as the representative CUF drop for each subsequent year starting from 11th to 25th year. (b) Estimated revenue loss @ Rs.4 per unit (kWh) for each subsequent year will be calculated as % CUF drop in the 10th year (as per (a) above) multiplied by the respective year’s estimated generation. (c) The Net Present Value (NPV) of the revenue loss for 10th to 25th year with discount factor of 8.30% will be considered as the LD payable by the Contractor.
| TECHNICAL SPECIFICATIONS | 282 of 309 | 1 (D), Annexure-2 | If the Contractor fails to achieve guaranteed annual CUF at the end of First Year, the Contractor shall pay compensation to the Owner (amount to be deducted from the Final Payment at the end of 1 year), an amount equal to the NPV of the estimated shortfall in cash flow resulting over the period of 25 years due to reduced Plant CUF, calculated at a tariff of Rs.3.5 per unit (kWh) and discount rate of 6.5%. The Contractor may take corrective action during the ensuing year to demonstrate the guaranteed CUF at the end of the 2nd year. In such case, the part of the Final Payment withheld by the Owner on account of Liquidated Damages shall be released and the CUF shall remain unchanged from the tender specifications. If the Contractor fails to demonstrate the guaranteed CUF at the end of 2nd Year as well, the CUF achieved at the end of First Year shall be fixed as the new Guaranteed CUF for the remaining period of this Contract.
72 | General |  |  | Dredging | Please confirm that no dredging required in reservoir | Technical-Civil | No dredging is required in the reservoir. Please refer Annexure-I Available Reservoir Area with Contour Details.
73 | SECTION – VII; CHAPTER-2; TECHNICAL SPECIFICATIONS | 133 of 309 | Cl. No. 31 | Power Evacuation System | Please inform if there are any railway crossing applicable for power evacuation | Projects | No such crossing shall be encountered
74 | Section VIII - General Conditions of Contract | 213 of 365 | Cl. No. 9.3 | The Contractor shall acquire and pay for all permits, approvals and/or licenses from all local, state or national government authorities | Except CEA other all approval shall be removed from bidder scope-Please confirm. | Contractual | The terms and conditions of the RfB shall prevail.
75 | TECHNICAL SPECIFICATIONS | 154 of 309 | 26.4 | As the ground water at site may not be suitable for construction and module cleaning purposes. Suitable water for construction and module cleaning purposes (during plant operation) by providing RO plant of requisite capacity including storage facilities shall be arranged by the bidder. | Water from the reservoir will be used for cleaning the PV modules, hence RO plant for cleaning of PV modules is not required. Kindly confirm | Technical-Electrical | Terms and conditions of the RfB shall prevail. Please refer Appendix A to Section VII, Chapter 2: Technical Specifications, C: Civil Works, Clause 26.7 for details.
76 | General |  |  | General Query | Kindly consider 3 years O&M instead of 10 years as per standard Industry practice | Technical-Electrical | O&M of the Plant under the Scope of the Contractor shall be for 5 years. Please refer S. No. of Amendment 1.
77 | General |  |  | General Query | As the PV modules will be mounted on Floaters, the module mounting structures is not applicable. Kindly confirm | Technical-Civil | Module Mounting Structure refers to any arrangement for mounting and fastening of PV Modules to the Floats
78 | Section VII | Page 21 of 144 | 5.1 | Inverter duty transformer shall be Dry Type or Oil Type (with Synthetic Ester or Natural Ester insulating oil) and shall comply with the latest edition of the following standards and codes including amendments, as applicable. In case of Oil type transformer with Natural Esters, the Transformer shall be hermetically sealed. | IEC 62975 ( Page 6 para 2, ) , IS 1180- 3 (Clause 3.2 ) allows use of natural ester in transformers with conservator and airbag. Attaching the relevant pages of the mentioned standards. We request you to kindly amend the clause to " Transformers shall be either hermetically sealed or shall have air cell inside the conservator" | Technical-Electrical | The terms and conditions of the RfB shall prevail.
79 | Section III | 64 / 365 | 1.1 | The bidders are required to meet following minimum functional requirements: • Performance Ratio (PR) – 84.4% • Capacity Utilization Factor (CUF) – 22.6% Module degradation factor, 0.5% per year | As per PVSyst, with respect with radiation, losses etc. we are achieving 81% PR. Request your intervention on the same. With 81% PR (with specific generation), we are able to achieve the AC CUF of 22.6% without margin. Hence we request to check and update the PR. As per industrial practice the Module degradation factor, 0.6% per year. Kindly accept. | Technical-Electrical | Module degradation shall be as per the approved OEM datasheet. Please refer Amendment 1.
80 | SOW | 8/309 | 2.18 | Statutory approvals required for setting up of the project: 1. Consent from the JUSNL /JBVNL for the evacuation of the power generated by Floating Solar Grid Interactive Floating Solar Power Projects. 2. Consent to establish the project during construction and consent to operate the project after the commissioning of the plant from Jharkhand Pollution Control Board (JPCB) 3. Approval of the Electrical Inspectorate, Government of Jharkhand for commissioning of the transmission line and the Floating Solar power project installed at the Project Site. 4. Certificate of Commissioning of the Floating Solar Grid Interactive Power Project issued by JBVNL. 5. SNA/JREDA registration certificate, if required. 6. Permission from all other statutory and no statutory bodies required for the Project. 7. Clearance from Department of Forest, Ecology and Environment, if required. | All the statutory approval are difficult to get from state authority. The bidders do not have much experience in state of Jharkhand. The delay in approval will hamper the project and in case any one of the approval. Hence, the bidder wish to take only CEA/CEIG approval only. Request to consider the plea as its onerous to get management approval. | Contractual | The terms and conditions of the RfB shall prevail.
81 | SOW | 9/309 | 2.19 | Water body approvals, agreement and charges, if any Consent/ Approval shall be sought from Water Resources Department, GoJ before construction | For bidder seeking water body approval will be very difficult. We request SECI to kindly seek approvals as it is easy for them. Request to consider the plea as its onerous to get management approval. | Contractual | The terms and conditions of the RfB shall prevail.
82 | SOW | 6/309 | 1 | Transmission Line from Plant till Interconnection Point: 132 kV Double Circuit with ACSR ZEBRA Conductor Protection Scheme at Power Evacuation Switchyard at Plant End: Over Current Earth Fault Protection along with Distance Protection and other required protection schemes | Since the project power has to be procured by State and the connectivity is to STU. The bidder has to anyhow to pay the supervision charges of transmission line to the authorities. In the state of Jharkhand the ROW of the transmission line is much more diffult due to ST lands etc. So, for the betterment of the project we request SECI to descope it from bidder's scope. Our management is hesitant to take this uncontrollable risk. Hence, request to kindly descope this TL and ROW from the bidder's scope. | Contractual | The terms and conditions of the RfB shall prevail.
83 | SOW | 8/309 | 2 | 10 (ten) years comprehensive operation and maintenance from the date of Operational Acceptance. | Comprehensive operation and maintenance 10 years means that the bidder has to take back to back warrantees and AMC from the suppliers. This will be having huge impact on pricing. Because of this the other PSU's go for 3 or 5 years of O&M. Hence we request SECI to reduce the O&M period. | Contractual | Kindly refer to Amendment 01.
84 | ANNEXURE 2 | 280/309 | D | LD for shortfall in Annual CUF | As per technical document 282/309, Rs.3.5 per unit (kWh) and discount rate of 6.5%. And in Liquidated Damages for Shortfall in Annual CUF for Solar PV Plant is Rs 4 kWH 355/365. Kindly confirm what we need to consider. | Technical-Electrical | Liquidated Damages for Shortfall in CUF shall be as per the Annexure 2 to the Annexure G: Operation & Maintenance Agreement of 100 MW (AC) Floating Solar PV Project at Getalsud Dam, Ranchi. 2 (D) (ii), Appendix 8. Functional Guarantees is amended. Please refer Amendment 1.
85 | TS Page 11 of 144 | 33/309 | 1.5 | Modules Warranty | In the tender the warranties is been stroked off. As per our understanding there is no warranties over modules. Kindly confirm. | Technical-Electrical | Please re-check. Module Warranty is applicable as per Clause 1.5 (Page 33 of 309)
86 | Section X – Contract Forms | 322/365 | PCC 13. Securities | Contract Performance Security (CPBG) First stage: 10% of the Contract - Value Valid for 90 days from Operational Acceptance of plant facilities. Second Stage: 5% of the Contract Value- Valid till 10th year of O&M from Operational Acceptance | As per industrial practice - for stage 1 - the CPBG of 3% is taken by other PSU' and 5% on O&M contract value. Request to kindly consider this. | Contractual | The terms and conditions of the RfB shall prevail.
87 | Section III | 64 / 365 | 1.1 | LD for shortfall in Annual CUF and PR | Request to kindly put a capping on LD on shortfall contractually as it should not open ended. Hence, request to consider the plea. | Contractual | The terms and conditions of the RfB shall prevail.
88 | Chapter-1 : Scope of Work | pdf page No. 5 of 309 | Clause-1 | Solar Inverter / Power Conditioning Unit Type - String | Please confirm whether we are open for Central Inverter | Technical-Electrical | No. Only String inverters are allowed. Please refer Project Particulars in Scope of Works.
89 | Chapter-1 : Scope of Work | pdf page No. 5 of 309 | Clause-1 | Minimum DC Capacity : 126 MWp | AC/DC Ratio is fixed as 1:1.26 or bidder are open to select to meet PR Requirement | Technical-Electrical | Plant DC capacity shall be proposed by the EPC Contractor during the detailed engineering to meet the guaranteed CUF as per the tender specifications. However, the minimum DC capacity shall be 126 MWp.
90 | Chapter-1 : Scope of Work | pdf page No. 12 of 309 | 4.9 | 33 kV Gas Insulated Switchgears including Vacuum Circuit Breakers, Current Transformers, Voltage Transformers, Relays and other accessories for complete protection of inverter transformer feeders suitable for installation on transformer floating platform. | Please confirm that whether bidder can select AIS 33kV Switchgear for ICOG, RMU, MV Switchgear. | Technical-Electrical | The terms and conditions of the RfB shall prevail.
91 | Chapter-1 : Scope of Work | pdf page No. 13 of 309 | 4.24 | Earthing system including earth strip/cables, earth electrodes, earth enhancing compound and all other associated materials for complete earthing of the plant. | Earthing rod at Inverter station (on the water) will be underwater type, so we have not considered earth enhancement compound. | Technical-Electrical | The terms and conditions of the RfB shall prevail.
92 | Chapter-1 : Scope of Work | pdf page No. 13 of 309 | 4.26 | LED luminaries with diffuser for indoor and outdoor illumination (off-shore and onshore), lighting poles, distribution boxes and power supply cables along with required conduits, fittings, etc. | Illumination system will be provided for Off-shore till PV Plant area only, but for On-shore Lighting system will be provided only in Inverter Station Area. Please confirm | Technical-Electrical | Illumination system will be provided for both off-shore and on-shore areas that are part of Plant Facility. Please refer Clause 24 of Section B: Electrical System of Technical Specifications.
93 | Chapter-2 : Technical Specification | pdf page No. 35 of 309 | 2.2 | Solar cable outer sheath shall be flame retardant, UV resistant and black in colour. Solar cable with positive polarity should have marking of red line on black outer sheath. | As DC cable will ON-SHORE ( above Water body), So, water blocking tapes under the armor is required or Not ? | Technical-Electrical | Cables shall be radially/transversally water blocked. Please refer Annexure O - Plan & Section of Cable Crossing to the TS (Refer S.No. No. Of Amendment 1)
94 | Chapter-2 : Technical Specification | pdf page No. 35 of 309 | 2.3 | DC cables shall be single core, armoured, Flame Retardant Low smoke (FRLS), PVC outer sheath conforming to IS 7098-II. DC cable with positive polarity should have marking of red line on black outer sheath. | Please confirm if FRLS required for DC cables. | Technical-Electrical | Yes.
95 | Chapter-2 : Technical Specification | pdf page No. 36 of 309 | 2.8.6 | Solar/DC cables shall be laid on the waterbed from PV Modules/SCB to inverter, if placed on shore. There shall be one spare run of cable per inverter. | We understand that bidder has to provide string Inverter and in that case there will be 3 core cable b/w Inverter to LT Panel. Pls clarify that we have to consider one spare run for this cable ? | Technical-Electrical | No, this clause is not applicable in case of String inverters which will be placed on floating platforms.
96 | Chapter-2 : Technical Specification | pdf page No. 43 of 309 | 5.1 | Inverter duty transformer shall be Dry Type or Oil Type (with Synthetic Ester or Natural Ester insulating oil) and shall comply with the latest edition of the following standards and codes including amendments, as applicable. In case of Oil type transformer with Natural Esters, the Transformer shall be hermetically sealed | a) Please confirm if bidder can opt for mineral insulating oil as per IS 335. b) Bidder is offering Inverter transformer with conventional tank if Natural ester insulating oil is in consideration. Pls accept. | Technical-Electrical | The terms and conditions of the RfB shall prevail.
97 | Chapter-2 : Technical Specification | pdf page No. 66 of 309 | 8.2 | Internal Arc Classification : IAC-A, FLR, System fault current for 1s | Bidder requests the internal arc type tested panel shall be applicable for indoor type panels only. This is not applicable for outdoor type panels placed in inverter floats. | Technical-Electrical | The terms and conditions of the RfB shall prevail.
98 | Chapter-2 : Technical Specification | pdf page No. 67 of 309 | 8.2 | Current Transformer : Accuracy Class 0.2 for metering (0.2S for metering at outgoing feeder), 5P20 for protection | At ICR Level ICOG/RMU, CT Accuracy class will be 0.5 and at MCR HT Switchgear will be 0.2 (incomer PV feeder) & 0.2s for metering (outgoing Feeder). Please confirm | Technical-Electrical | The terms and conditions of the RfB shall prevail.
99 | Chapter-2 : Technical Specification | pdf page No. 67 of 309 | 8.2 | Voltage Transformer : 0.2 for metering, 3P for protection | At ICR Level ICOG/RMU, PT Accuracy class will be 0.5 and at MCR HT Switchgear will be 0.2 (incomer PV feeder) & 0.2 for metering (outgoing Feeder). Please confirm | Technical-Electrical | The terms and conditions of the RfB shall prevail.
100 | Chapter-2 : Technical Specification | pdf page No. 67 of 309 | 8.3.3 | The panel enclosure shall be constructed with CRCA steel/Aluzinc sheet. The thickness of load bearing members shall be minimum 3 mm and that of non-load bearing members shall be minimum 2 mm. | Switchgear Panel material & thickness will be as per OEM type tested design Only. | Technical-Electrical | Ok. Please refer Amendment 01.
101 | Chapter-2 : Technical Specification | pdf page No. 68 of 309 | 8.3.10 | Panel shall be provided with local bus-bar protection. | We have not envisaged any Bus bar protection at 33kV level. Please confirm | Technical-Electrical | The terms and conditions of the RfB shall prevail.
102 | Chapter-2 : Technical Specification | pdf page No. 70 of 309 | 8.5.8 | Each feeder shall have two lock out relays powered through two independent DC supplies. Each lock out relay shall send through two separate potential free output contacts signals to each of the two independent trip coils. | Bidder is proposing that each feeder will have only one Lock Out relay with one independent DC supply. | Technical-Electrical | The terms and conditions of the RfB shall prevail.
103 | Chapter-2 : Technical Specification | pdf page No. 80 of 309 | 10.2 | All AC cables shall be flame retardant, low smoke (FRLS) type designed to withstand all mechanical, electrical and thermal stresses develop under steady state and transient operating conditions. | Please confirm if FRLS required for all AC cables. ? Also Please confirm water blocking tapes under the armor required or Not ? | Technical-Electrical | Yes, all AC Cables shall be FRLS type as per specifications. Cables shall be radially/transversally water blocked. Please refer Annexure to the TS (Refer Amendment 01)
104 | Chapter-2 : Technical Specification | pdf page No. 81 of 309 | 10.5.(iii) | Short circuit withstand capability as per design for 1s | Cable short circuit withstand will be sized as per Relay coordination study. Please confirm | Technical-Electrical | The terms and conditions of the RfB shall prevail.
105 | Chapter-2 : Technical Specification | pdf page No. 81 of 309 | 10.8.4 | In case of string inverter, AC cables from inverter to AC Combiner Panel shall be laid through UV resistant Double Wall Corrugated HDPE conduits. The size of the conduits shall be selected on the basis of 40% fill criteria. The conduits shall be routed through closed cable trays fixed on top of the floats on the PV Module floating platform. The conduits shall be routed on top of dedicated floats (on-shore) from PV Module floating platform through appropriate support structure till transformer. Conduits shall be tied to the cable trays at regular intervals using UV resistant cable ties. | AC cable will be laid through ladder tray over floater with cable tie. Please confirm | Technical-Electrical | Please refer Amendment 1.
106 | Chapter-2 : Technical Specification | pdf page No. 82 of 309 | 11.3 | Auxiliary system shall be provided with two independent sources for reliable auxiliary power supply. | Bidder proposes two incomer scheme with Bus coupler for Main control room ACDB. However for inverter station ACDB shall have only one connections from LV side of the inverter transformer. | Technical-Electrical | Agreed.
107 | Chapter-2 : Technical Specification | pdf page No. 82 of 309 | 11.4 | Following consideration shall be taken into account while sizing the auxiliary transformer: (I) 20% future load margin (ii) 20% design margin (iii) Total connected load at 0.8 power factor | Bidder request 20% future load margin & 20% design margin for Main control room. For Inverter station we are not considering any margin in the auxiliary transformer sizing. | Technical-Electrical | Agreed.
108 | Chapter-2 : Technical Specification | pdf page No. 90 of 309 | 15.1 | Lightning Protection System (LPS) for the entire plant (off-shore and on-shore) against direct and indirect lighting strokes shall be provided as per IS/IEC 62305:2010. | Bidder request to accept Early streamer type LA for array area, ICR with protective radius of 107 M. | Technical-Electrical | The terms and conditions of the RfB shall prevail.
109 | Chapter-2 : Technical Specification | pdf page No. 125 of 309 | 24.4.11 | Suitable illumination system shall be provided along the floating fence | Is Illumination to be provided at entire periphery of FSPV array area or only at OFF-SHORE for MCR & Switchyard periphery. Please clarify | Technical-Electrical | Illumination shall be provided at on-shore for the MCR and Switchyard periphery. In addition, the bidder shall propose suitable illumination for the Floating Transformer Platform and floating platforms (float corner points)
110 | Chapter-2 : Technical Specification | pdf page No. 128 of 309 | 28.1 | CCTV Cameras along with monitoring station and all other accessories required for its proper operation must be installed to have complete coverage of following areas for 24 hours. (I) Main Control Room: Covering Entry/Exit and Equipment Rooms (ii) Switchyard (iii) PV Module Floating Platform & Transformer Floating Platform (iv) Main entry: covering all entry/exits (v) Along the Plant Perimeter: Covering complete perimeter of Plant Area to capture all possible intrusion (vi) Security Cabin | Bidder has considered CCTV at I) MCR entry /exit ii) Switchyard iii) Transformer Floating Platform only. | Technical-Electrical | Agreed. Please refer Amendment 01
111 | Chapter-2 : Technical Specification | pdf page No. 155 of 309 | 26.9 | The water supply mains shall be of HDPE material with suitable UV resistant additives.. | We have not considered separate floaters for water piping system. | Technical-Civil | The terms and conditions of the RfB shall prevail.
112 | Chapter-3 : Special Technical Conditions | pdf page No. 168 of 309 | 3.2 | Maximum block size for the FSPV plant shall not be higher than 4 MW (AC). Blocks shall be symmetrical in shape. | Please confirm if we can propose 4.4 Mwac Block size. | Technical-Civil | Please refer Amendment 01
113 | Chapter-2 : Technical Specification | pdf page No. 154 of 309 | 26.2 | A regular supply of suitable quantity of water shall be ensured by the Contractor to cater day-to-day requirement of drinking water and for cleaning of PV modules during entire O&M period. | Bidder request to accept to use DAM water at free of cost for cleaning. And please clarify the requirement of RO and suggest location of the RO plant. | Technical-Electrical | Please refer Clause 26.7 for details of the PV Module Cleaning System. Location of the RO Plant shall be proposed by the EPC Contractor during detailed Engineering.
114 | Chapter-2 : Technical Specification | pdf page No. 159 of 309 | 28.22.1 | The floating platform shall be made of HDPE/FRP or precast or cast in-situ fixed platform and shall be of adequate size for installation of equipment, associated facilities, movement and working of O&M personnel, etc. | Bidder request to accept Ferro cement floats. | Technical-Civil | Please refer Amendment 01
115 | General |  |  |  | Bathymetry report: Please provide ANNEXURE - M | Technical-Civil | Please refer Annexure I: Available Reservoir Area with Contour Details. (Refer Amendment 01)
116 | General |  |  |  | Please Provide the Coordinates for 132/33 IRBA GSS | Technical-Electrical | Please refer Annexure L - Tentative Route Map for Transmission Line
117 | General |  |  |  | Please provide the reservoir usable area CAD file. | Technical-Civil | Please refer Amendment 01
118 | General |  |  |  | Please provide the MCR & Plant end Substation Location. | Technical-Electrical | Please refer Annexure O - Plan & Section of Cable Crossing
119 | General |  |  |  | Please provide the SLD & LAYOUT of remote end substation. Please confirm the Scope of Works for remote end Substation | Technical-Electrical | The EPC Scope of Work includes interconnection with the existing Bays (111 and 112) at the Grid Substation.
120 | General |  |  |  | Floating Solar PV Array Layout: Please confirm after how many rows Pathways are to be provided. | Technical-Civil | Please refer Amendment 01
121 | General |  |  |  | Please confirm the site temperature details | Technical-Civil | Please refer Amendment 01
122 | General |  |  |  | Please provide the KMZ file | Technical-Civil | Please Refer Annexure I: Available Reservoir Area with Contour Details. (Refer Amendment 01)
123 | CHAPTER -2 TECHNICAL SPECIFICATIONS | Page-32 of 309 | 1.4.1 The PV Modules glass panel: | It shall be laminated using a laminator with symmetrical structure, i.e., heating plates on both sides. | Bidder clarifies that laminator heating plate shall be as per manufacturer machine standard, specific machine type requirements for lamination will restrict suppliers, bidder requests to amend this clause. | Technical-Electrical | The terms and conditions of the RfB shall prevail.
124 | CHAPTER -2 TECHNICAL SPECIFICATIONS | Page-33 of 309 | 1.4 Component Specifications-1.4.6 | RFID code scanner and database of all the modules containing the above information shall also be provided. | Internal- Cost adder to be considered | Technical-Electrical | Query not clear
125 | Annexure – A | Page-174 of 309 | 5. Scope of Inspection: Witness Tests: | IV. Electrical Characteristics (Other than Flash Test)- As per Sampling Plan | The bidder understands the Electrical Characteristics test stands for - Hi-pot test, other than flash tests. | Technical-Electrical | Please refer Annexure-A - PV Module Pre-dispatch Inspection Protocol to the TS for details.
126 | Annexure – A | Page-174 of 309 | 6. Sampling Process: | Note: Smallest lot size for Inspection: 20% of the capacity as per the PO. | The bidder requests to consider 1 lot size of minimum 10MWp. | Technical-Electrical | Please refer Amendment 01
127 | Annexure – A | Page-174 of 309 | 6. Sampling Process: | c. Same samples shall be used for all Witness Tests stated at 5.2 above. | This clause is missing from the document, contractor understands that the above mentioned test under witness test is the same. Please confirm. | Technical-Electrical | Please refer Amendment 01
128 | Annexure – D | Page-227 of 309 | 5.1 INFRARED INSPECTION | o PV modules: 100% o Inverters: 100% o Combiner boxes: 100% | Internal- Cost adder to be considered | Technical-Electrical | Query not clear
129 | Annexure – D | Page 217 of 309 | 3.1.2 General Requirements before Starting the Commissioning Process | Electroluminescence camera, power supply and accessories | The bidder requests not to consider EL inspection at site, hence EL camera shall not be considered. | Technical-Electrical | Please refer Amendment 01
130 | Annexure – D | Page 229 of 309 | 5.3 SINGLE AXIS TRACKER AVAILABILITY TEST (IF APPLICABLE) | The tracker availability test shall be carried out in parallel to the inverter availability test and shall have the same duration. | The bidder requests not to consider separate tracker availability guarantee if applicable for the project. However, if required, it shall be back to back from the tracker manufacturer considered for the project. | Technical-Electrical | Tracker is not applicable to the Project.
131 | ANNEXURE 2 Functional Guarantees | Page 280 of 309 | 1. Annual CUF Guarantee | The Contractor guarantees the annual CUF committed herein over the O&M Period (“Annual CUF Guarantee”) from the date of Operational Acceptance. | The bidder requests to consider Performance Ratio as plant performance assessment parameter for annual O&M periods. | Technical-Electrical | The terms and conditions of the RfB shall prevail.
132 | Annexure – C | Page 207 of 309 | 2.1 PERFORMANCE RATIO GUARANTEE TEST | Tref PV Module temperature at which Po is determined, i.e. 25°C | The bidder requests to consider Tref as monthly average module temperature calculated from the hourly PVSYST weather file for the project, to be considered for the month in which PG test is conducted. | Technical-Electrical | The terms and conditions of the RfB shall prevail.
133 | Annexure – C | Page 207 of 309 | 2.1.2 General Requirement | During this PR test, equipment failure/interruption of any kind, except for SCADA communication failures, will not be accountable. | The bidder requests to include following events excluded from performance ratio test periods: periods in which because of any fluctuation or disturbance of the grid, the protection of the Plant is open, or the inverters shut down;  periods in which the Plant is not able to generate because of grid unavailability;  periods of interruption or distortion of the Plant’s Generation caused by the Owner/third party/compliant authority.  Periods of inverter clipping during periods of higher insolation beyond that considered in design.  Periods of power curtailment and load shedding  Grid failure beyond Contractor’s control In case of Loss due to lower rated voltage of grid, Inverter performance shall be affected and such time period will be excluded  In case of tracker, an occurrence of a high wind event which causes any number of trackers to enter emergency stow position. Only those number of trackers impacted from high wind event will be excluded in such case.  Any Losses on account of a Power Factor other than Unity Power Factor shall be adjusted for the purpose of calculation of estimated PR %. | Technical-Electrical | Please refer Clause 2.1.4.3 for Data Filtering conditions
134 | Annexure – C | Page 210 of 309 | 2.1.5 Determination of PR Test | Radiation Criteria – Radiation on Plane of Array (POA) less than 200 W/m2 | The bidder requests to consider that periods when the average radiation in the plane of the array of the Plant is below 50W/m2 shall be excluded from PR test calculation. | Technical-Electrical | The terms and conditions of the RfB shall prevail.
135 | Appendix A to Section VII | 13 | 4.27 | Weather monitoring station shall include but not be limited to the following  Pyranometers – Two in Horizontal Plane for GHI and two in inclined plane for GTI – Minimum 4 (Four) Nos.  Ultrasonic Anemometer (wind speed and direction) – 2 (two) no.  Temperature Sensor (ambient and module surface) – 3 (three) nos.  Power source to the all sensors wherever required  Data Logger | Please confirm that only indicated sensors need to consider in WMS and also confirm that how many WMS need to provide for complete capacity of plant. | Technical-Electrical | 3 No. of Weather Monitoring Stations as per this Clause shall be provided at discrete locations. Please refer Amendment 01.
136 | Appendix A to Section VII | 13 | 4.16 | FOTE | Please provide the specs for FOTE | Technical-Electrical | Please refer Annexure P - Approved FOTE Specifications - GA, GTP, BOQ, Layout and Scheme Drawings.
137 | Appendix A to Section VII | 72 | 8.9.1 | All the measuring instruments shall be digital, flush mounting type with communication facility. Meters at 33 kV and above voltage level shall be IEC 61850 compliant for communicating with the SCADA system. | We are proposing the meters at RS485/TCP-IP and relays at IEC-61850 at 33kV and above voltage level, please accept. | Technical-Electrical | The terms and conditions of the RfB shall prevail.
138 | Appendix A to Section VII | 70 | 8.5.14 | The numerical relays and meters at 33kV and above voltage level shall be IEC 61850 compliant for communicating with the SCADA system. | We are proposing the meters at RS485/TCP-IP and relays at IEC-61850 at 33kV and above voltage level, please accept. | Technical-Electrical | The terms and conditions of the RfB shall prevail.
139 | Appendix A to Section VII | 92 | 18.1.3 | Support for O&M Activities: The interface shall allow integration with Module Cleaning System and various other O&M support systems to provide a Data Analysis and Decision Support System for smooth and efficient Plant Operations. | Please specify that what are the other O&M support systems which need to provide a Data Analysis and Decision Support System for smooth and efficient Plant Operations since accordingly will consider the system. | Technical-Electrical | O&M Support systems for Data Analysis and Decision Support System includes features to Visualize and categorize events affecting solar plant performances, link to Plant Maintenance Schedules etc.
140 | Appendix A to Section VII | 93 | 18.2.3 | Analog and Digital IO modules shall have integrated processor for distributed IO processing and control. | Does remote IO is referred as distributed IO, please confirm. If not, so please elaborate on it. | Technical-Electrical | The Clause specifies IO modules with integrated processor for distributed processing.
141 | Appendix A to Section VII | 93 | 18.2.6 | Plant data for monitoring and control operations should be accessible without dependence on external network. | Remote server may requires the external network for Monitoring and control operations of plant since to access the cloud and remote server will requires the internet. Please confirm. | Technical-Electrical | The Clause is applicable to Plant Server.
142 | Appendix A to Section VII | 93 | 18.2.8 | Operator Workstation/PC shall be of Industrial Grade for browser-based access to plant data from Plant or remote server. Plant control & SLDC/Utility related operations shall only be initiated through browser based interface requiring no client software or database to be installed on the Workstation. All critical software and Plant Data shall be installed/stored on local and remote servers only with user access control for protecting the software and data assets from accidental deletion or corruption. | Please confirm that in this case conventional OWS function is required or not and how browser based access will be done either will it be through the static IP or by another mode. | Technical-Electrical | Yes, OWS is required. Please refer Clause 18.9. It will be accessed through static IP.
143 | TENDER TECH SPEC. | 2 | Index | Annexure | In technical specification document, Annexure ( H to M) is missing. Please provide | Technical-Electrical | Please refer Amendment 01.
144 | TENDER TECH SPEC. | 6 | 1 | Transmission line 132 kV Double Circuit with ACSR-ZEBRA Conductor | It is understood there is 132 kV double circuit transmission tower with single line shall be considered PSS to GSS tower. | Technical-Electrical | Yes
145 | TENDER TECH SPEC. | 76 | 9 | 33kV GIS( Gas Insulated Switchgear) | Please confirm if AIS can be provided for MCR Switchgear in place of GIS | Technical-Electrical | Yes. Please refer Clause 4.10 of Scope of Works
146 | TENDER TECH SPEC. | 118 | 23.7.3.1 | …..metering CTs of ratio less than 400/1. | For line bay 400/1 is not sufficient with evacuation of 100 MW power, however we are considering adequate number of 500/1 A CT | Technical-Electrical | Agreed.
147 | TENDER TECH SPEC. | 86 | 13.3.4 | Auxiliary DC system voltage | Please confirm the DC system voltage | Technical-Electrical | To be decided during detailed engineering
148 | TENDER TECH SPEC. | 110 & 168 | 23.4: &1 | Seismic level | In design consideration table seismic zone II considered however in 132 kV circuit breaker technical parameter table Cl 23.4.1 seismic V mentioned. Please confirm. | Technical-Electrical | Please refer the Clause. The Clause mentions Seismic levels for sites in Zone V as well as sites other than in Zone V
149 | TENDER TECH SPEC. | 10 | 4.14 | ABT meters with all necessary metering rated CTs and PTs at 132 kV side of Plant Substation as per CEA Metering Regulations 2006 | Please note that ABT meter (Stand By) shall be considered with required CTs & PTs in Line bay as per CEA Metering Regulations 2006. | Technical-Electrical | Agreed.
150 | TENDER TECH SPEC. | 11 | 4.15 5.12 | NOTE : The Contractor shall construct the line after Joint Detailed Survey of Transmission Line Route Jointly Verified by the representatives of SECI and JUSNL. Supervision Charges payable to JUSNL shall be borne by SECI. Installation, Testing and Commissioning of 132 kV Double Circuit Transmission Line from Plant Substation to Interconnection point. | It is understood that considering transmission line scope only Installation, Testing and Commissioning of 132 kV Double Circuit Transmission Line from Plant Substation to Interconnection point shall be considered. However, providing right of way, its applicable clearance and rehabilitation if required shall be out of EPC scope. Please confirm the understanding. | Technical-Electrical | Installation, Testing and Commissioning of 132 kV Double Circuit Transmission Line from Plant Substation to Interconnection point, including RoW, clearances etc. shall be in the Scope of the EPC Contractor.
151 | TENDER TECH SPEC. | 12 | 4.35 | Any other equipment / material, not mentioned but required to complete the Solar Power Plant facilities in all respect. | Any other equipment / material, not mentioned but required to complete the Solar Power Plant facilities in all respect within scope limit from floating solar to POI at GSS tower. | Technical-Electrical | Agreed.
152 | TENDER TECH SPEC. | Page 6 of 144 | A Design Philosophy, 1.8 | System design shall have intelligent protection mechanism which may include very fast responsive microprocessor-based relays etc., | Please note that network relay with applicable protection having communication protocol with IEC61850 shall be considered. Please confirm. | Technical-Electrical | Please refer Section B: Electrical System for relevant Technical Specifications
153 | TENDER TECH SPEC. | Page 30 of 144 | A Design Philosophy, 5.3.4.3 | Special Tests: (iv) Short-circuit withstand test as per IEC 60076-5 | Please note that short circuit calculation shall be furnished instead of actual test conduction. Kindly accept. | Technical-Electrical | Short-Circuit Withstand Test on proposed equipment or similar equipment shall be accepted. Terms and conditions of the tender shall prevail.
154 | TENDER TECH SPEC. | Page 30 of 144 | 7.6.1 | Bus bar shall be made of copper or aluminium with uniform cross section…. | Please note that busbar shall be considered made of aluminium. | Technical-Electrical | The terms and conditions of the RfB shall prevail.
155 | TENDER TECH SPEC. | Page 3 of 20 | SOW : 1 Project Particulars | Interconnection Point : Bay -111 & Bay-112 of 132/33 kV IRBA GSS (JUSNL) | It is understood that one line of pooling substation shall be interconnect to either of 2 Nos available bays i.e. Bay -111 & Bay-112 of 132/33 kV IRBA GSS (JUSNL). Please confirm. For reactive power compensation CEA guideline has to be followed. We understand that the PR has to be shown at solar plant substation. so the reactive power compensation by CEA for Inverter capacity has to be at solar plant substation. Please confirm. | Technical-Electrical | Interconnection with the GSS is over Double Circuit Transmission line, one circuit to be connected at each bay (111- and 112). PR is to be demonstrated at the Plant End. Reactive Power Compensation shall be at the Point of Interconnection i.e. the GSS end as per the CEA Technical Standards for Connectivity
156 | TENDER TECH SPEC. | - | GENERAL | FOTE, SCADA and Differential really requirement at GSS Substation | Please note that FOTE, SCADA and Differential relay requirement at GSS Substation has not been considered in scope. Please confirm | Technical-Electrical | FOTE, SCADA to be provided at the Plant End Substation as per the Scope of Work. Please refer Annexure P - Approved FOTE Specifications - GA, GTP, BOQ, Layout and Scheme Drawings.
157 | TENDER TECH SPEC. | - | GENERAL | Type test reports | Bidder proposes Type test report for last 10 years as per CEA guidelines | Technical-Electrical | Please refer specific clauses in the Technical Specifications. The terms and conditions of the RfB shall prevail.
158 | TENDER TECH SPEC. | - | GENERAL | Current density | Bidder proposes max current density will be 3.5A/sqmm at nominal voltage incase of Cu trafo and 2A/sqmm for Al trafo. | Technical-Electrical | The terms and conditions of the RfB shall prevail.
159 | TENDER TECH SPEC. | - | GENERAL | Panel construction. | All 415V LT panel shall be form 2B type as no separate segregation is possible with MCB. | Technical-Electrical | The terms and conditions of the RfB shall prevail.
160 | TENDER TECH SPEC. | - | GENERAL | Office : 300 Lux | Bidder proposes Lux level for SCADA and Admin rooms shall be avg 250 lux and rest rooms in MCR shall be 100 Lux. | Technical-Electrical | The terms and conditions of the RfB shall prevail.
161 | TENDER TECH SPEC. | - | GENERAL | 145kV Circuit Breaker | For Transformer and bus coupler 3 pole (Mechanically Ganged) Circuit breaker without auto recloser feature is considered | Technical-Electrical | PGCIL approved components shall be used for construction of 132 kV switchyard. Terms and conditions of the tender shall prevail.
162 | TENDER TECH SPEC. | - | GENERAL | 145kV Circuit Breaker | For Line bays 1 Pole (Electrically Ganged) Circuit breaker with auto recloser feature is considered | Technical-Electrical | PGCIL approved components shall be used for construction of 132 kV switchyard. Terms and conditions of the tender shall prevail.
163 | TENDER TECH SPEC. | - | GENERAL | Support Structure | PGCIL approved substation structures for tower, beams and equipment support structures is considered | Technical-Electrical | The terms and conditions of the RfB shall prevail.
164 | TENDER TECH SPEC. | - | GENERAL | DG Set | DG set is not considered. | Technical-Electrical | The terms and conditions of the RfB shall prevail.
165 | TENDER TECH SPEC. | - | GENERAL | Future expansion | Beam and tower for future transformer bay is not considered in base scope. | Technical-Civil | Not considered
166 | Table of Contents | 2 |  | Annexure H, I , K ,M Annexure J Bore Hole Locations and Bore Holes Logs | Annexures missing in the Technical Document. SECI to share Detailed Geotech report to be shared including soil and water chemical analysis, SBC calculations, CBR values, pile capacity calculation etc. to be shared. | Technical-Civil | Please refer Amendment 01.
167 | 1. Project Particulars | 6 |  | Bathymetric Survey Report Carried Out by SECI (2020) – Excerpts from the Report enclosed as Annexure M | Annexure-M missing in technical document. Please share | Technical-Civil | Please refer Annexure I: Available Reservoir Area with Contour Details. (Refer S. No. of Amendment)
168 | 2 Brief Scope of Works | 8 | 15 | Highest water level of reservoir n the year 1998 – 590.09m (Reached FRL) In the year 2006 – 590.40m (Crossed FRL) In the year 2017 – 590.49m (Crossed FRL) | As per our understanding the water level should not rise beyond FRL as any raise above FRL shall be automatically discharged through spillway. Please confirm. | Projects | Yes
169 | 2 Brief Scope of Works | 17 | 17 | Water flow velocity at tentative project location Maximum velocity value shall be considered after performing flood routing studies using software simulations or hydraulic model study to derive flow path and critical velocities. Additionally, water current velocity shall be measured at upstream and downstream of proposed site for at least 30 days using suitable Acoustic Doppler Current Profiler (ADCP) /Current Meter. The velocity measurements should be undertaken at surface, at half of the water depth, and at 0.5 m above the reservoir bed. | Please confirm the relevant authority which can provide the previous years data for performing the flood routing study and data pertaining to water current velocity and wave heights etc. | Projects | Water Resources Department, Govt. of Jharkhand
170 | 3 Design and Engineering | 9 | 3.2 | All documents and drawings (soft copy) shall be submitted to the Employer for review and approval. Every drawing shall also be submitted in ‘*.dwg’ format. In case of design calculations done in spread sheet, editable (working) soft copy of the spread sheet shall also be submitted along with ‘pdf’ copies during every submission. The Employer shall return to the Contractor with category of approval marked thereon. Five nos. of hard copies of approved documents and drawings shall be submitted to the Employer. | As per company policy SWREL does not share source file (AutoCAD, Excel etc), however detailed documents shall be provided in pdf format. CAD file of Layout shall be shared. | Technical-Civil | The terms and conditions of the RfB shall prevail.
171 | 3 Design and Engineering | 10 | 3.3 | Design calculations and design templates for Floats, Anchoring and Mooring mechanism | Please share the anchor and mooring system material specification | Technical-Civil | Please refer Cl. 28.15 of TS.
172 | 6 Civil Works | 16 | 6.1 | Conducting topographical survey of on-shore portion of the plant area including submission of contour drawings. | The CAD file for Plant area(On shore) and reservoir area to be shared along with KMZ file. | Technical-Civil | Please Refer Annexure O - Cable Crossing, Sections and Switchyard Location to Technical Specifications
173 | 6 Civil Works | 16 | 6.8 | Construction of outdoor storage shed of area sufficient enough to store spares. | Please confirm the min. area to be considered and min. technical requirements of same | Technical-Civil | Please refer Amendment 01
174 | 6 Civil Works | 17 | 6.14 | Construction of Transformer floating platform including floating system, anchoring and mooring system. | Please confirm if there is any fencing requirement for Floating Transformer foundation and its related accessories. | Technical-Civil | Floating system/platform for modules shall be fenced with vacant floats to demarcate boundary. For floating System for transformer & other equipment's the fence with vacant floats is not required, but shall be provided with hand rails as per Cl. 28.22.5.
175 | 6 Civil Works | 17 | 6.15 | Construction of floating fence around off-shore portion of the plant. | Please confirm the min. technical requirement of same in terms of material required, height etc. and whether it is above/below the water level. Please share tender drawing for same for clarity. Please also share the purpose of provision of same. | Technical-Civil | Floating system/platform for modules shall be fenced with vacant floats to demarcate boundary. For floating System for transformer & other equipment's the fence with vacant floats is not required, but shall be provided with hand rails as per Cl. 28.22.5.
176 | 6 Civil Works | 17 | 6.18 | Construction of storm water drainage & sewage network including rain water harvesting mechanism (on-shore). | a) Please share the hydrology report of the area if available. b) Also confirm he min. requirements of drain cross-section, side slope, material requirements etc. c) Also share typ. Drawing for Rain water harvesting system to be considered along with min. nos. of same required. | Technical-Civil | a) Please refer Annexure-I Available Reservoir Area with Contour Details b) Refer Amendment 01 c) Refer Amendment 01.
177 | 6 Civil Works | 17 | 6.23 | Construction of approach path (RCC/Steel framed structure) to facilitate movement of personnel and equipment from the reservoir bank to the floating platform provided for access to the boat/vessel. This floating platform shall be located where adequate water depth is met at MDDL for the movement of boat/vessel and shall be suitably anchored. | Please confirm the min. length to be considered for same and share typ. Tender drawing if any for clarity on same. | Technical-Civil | Please refer Amendment 01. The details shall be as per project requirements.
178 | 8 Operation and Maintenance | 19 | 8.8 | To upkeep all administrative offices, equipment rooms, roads, vehicular parking, tool room, stores room, equipment, clean, green and in workable conditions. | Please confirm the no. of vehicles to be considered including min. requirements for Vehicular parking | Projects | Parking facilities for 2 nos. of Four Wheelers and 10 Nos. of Two Wheelers may be provided.
179 | 5 Geotechnical & Geophysical Investigations | 139 | 5.3 | The field investigations shall mainly include drilling of min. 7m deep borehole (for onshore) & 10m deep borehole (for off-shore For the off-shore investigation, there shall be min. 1 no. of BH for every 10 acres of selected site. | SWREL suggest The field investigations shall mainly include drilling of min. 7m deep borehole (for onshore) & 7m deep borehole (for off-shore. Please confirm For the off-shore investigation, there shall be min. 1 no. of BH for every 15 acres of selected site. Please confirm | Technical-Civil | The terms and conditions of the RfB shall prevail.
180 | 7. Roads & Access Pathways: | 141 | 7.1 | Suitable approach road (as applicable) from nearest public road up to Main gate(s) and Landing Area adjacent to the reservoir, Access road from Main gate to Control Room Buildings(office building and Equipment Building), Internal roads connecting Control Room Buildings and other facilities, Sub-station & Switch yard (as applicable) etc., Peripheral road all around Sub-station Area shall be provided for safe and easy transportation of men, material and equipment during construction and subsequent operation & maintenance (O&M). | a) Please share the plant boundary along with location of nearest public road, MCR location, Substation / Switchyard location b) Peripheral Road carriageway and shoulder width to be confirmed | Technical-Civil | a) Please refer Annexure O: Cable Crossing, Sections and Switchyard Location to TS (Refer Amendment 01) b) Please refer Amendment 01
181 | 9 Peripheral boundary Fence / Wall & Main gate | 144 | 9.5 | The founding depth (below NGL) for the precast column shall be min. 800 mm and the column shall be embedded in PCC (1:2:4) block of 600 mm x 600 mm. | SWREL suggests: The foundation for precast column shall be with M20 grade concrete with 350 dia pile and 800mm deep below NGL | Technical-Civil | The terms and conditions of the RfB shall prevail.
182 | 9.7 Main gate | 144 | 9.7 | Main Gate shall be provided as per the indicative drawing titled ‘Entrance Gate Drawing’ provided in Annexure-K: Tender Drawings. | Annexure K missing in Technical document. Please share | Technical-Civil | Please refer Amendment 01
183 | 9.8 Floating Fence | 145 | 9.8 | Floating fence with floating buoys (with durable UV resistant material suitable to withstand the aqueous environment, be eco-friendly to bio diversity, and withstand pressure of debris/trees/flotsam through river during monsoon period) shall be formed around every floating platform. | Please share Conceptual tender drawing for same for understanding the requirements in terms of height, material etc. | Technical-Civil | Floating fence shall comprise of vacant floats and shall fulfil the requirements stated under the Clause.
184 | 11 Design Loads | 147 | 11.6 | To calculate the design wind speed (Vs.), the factors K1 (probability factor or risk coefficient), K2 (terrain roughness and height factor) and K3 (topography factor) shall be considered as per IS 875 (Part-3). (However, minimum values for K1, K2 and K3 shall be 1.0, 1.05 and 1.0 respectively) | a) For plant design life of 25 years, K1 = 0.92 can be considered for basic wind speed of 39m/s. Please confirm. b) Also confirm if 20% reduction in wind pressure can be considered owing to str. height less than 10m. c) Confirm if the design shall be done considering uniform loading for wind. | Technical-Civil | a) Terms and conditions of the RfB shall prevail. b) Please refer Amendment 01. c) Wind load shall be evaluated using CFD Analysis.
185 | 11 Design Loads | 147 | 11.7 | In case of plant site within 60 km of sea coast, the importance factor for cyclonic region, ‘K4’ shall be taken as 1.15. | K4 shall be considered as 1, since the sea coast is not applicable here. Please confirm | Technical-Civil | Agreed
186 | 11 Design Loads | 147 | 11.8 | To calculate the design wind pressure ‘pd’, factors ‘ka’ (area averaging factor) and ‘kc’ (combination factor) shall be taken as 1.0. (The factor ‘kd’ shall be taken as 1.0 in case of plant site within 60km of sea coast).n as 1.15. | Kd shall be considered as 0.90 as per IS -875 3 requirements since the plant location is far away from sea coast | Technical-Civil | Agreed
187 | 13 Concrete Works | 148 | 13.6 | Reinforcement steel shall be of high strength TMT bars of grade Fe500 D conforming to IS: 1786 with anti-corrosive coating to withstand aqueous environment. Ductile detailing in accordance with IS: 13920 shall be adopted for all RCC buildings. | Please confirm the corrosion category to be confirmed. Also confirm the concrete exposure to be considered as per IS 456 for understanding the requirement of anti-corrosive coating for reinforcement. | Technical-Civil | Refer Amendment 01.
188 | 25 Transformer Yard Civil Works | 153 | 25.6.1 | The fencing shall be of galvanized iron chain link mesh fabric with internal, corner and stay posts of hot dipped GI angle (min. ISA 65x65x6 mm) with 100mm thick M15 PCC foundation (min. width 450mm and min. depth 450 mm below GL). | PCC foundation requirement is not clear. Is this requirement is for toe wall. Please confirm | Technical-Civil | Requirement is for the toe wall. Refer Amendment 01.
189 | 25 Transformer Yard Civil Works | 153 | 25.6.3 | Spacing of intermediate posts shall not be more than 2.5m. Every 10th intermediate post shall be provided with a stay post while every corner post shall be provided with two stay posts on either side. | Bidder suggest Recommended spacing of intermediate post shall be 3m. Kindly Confirm | Technical-Civil | The terms and conditions of the RfB shall prevail.
190 | 26 Water Supply and Cleaning of Modules | 154 | 26.4 | As the ground water at site may not be suitable for construction and module cleaning purposes. Suitable water for construction and module cleaning purposes (during plant operation) by providing RO plant of requisite capacity including storage facilities shall be arranged by the bidder. | Please confirm is the RO plant shall be Off shore or onshore | Technical-Civil | RO Plant may be installed onshore or offshore as per the finalised layout during detail engineering.
191 | 28 Floating System | 159 | 28.22.1 | The floating platform shall be made of HDPE/FRP or precast or cast in-situ fixed platform and shall be of adequate size for installation of equipment, associated facilities, movement and working of O&M personnel, etc. | bidder wants to explore use of ferro-cement for platform for durable and optimized solution. Please confirm | Technical-Civil | Please refer Amendment 01
192 | 28 Floating System | 159 | 28.22.5 | The Handrails of Stainless steel (SS316) of minimum 1 m height should be provided all around the floating platform. Step ladder for access from boat or land with handrail to the platform shall also be provided. | Shall handrail be provided after the floating fence. Please confirm the location | Technical-Civil | For floating System for transformer & other equipment's the fence with vacant floats is not required. Other requirements shall be as per terms and conditions of the tender.
193 | Laboratory and Field Testing | 162 | 3.1 | The Laboratory building shall be constructed and installed with adequate facilities to meet the requirement of envisaged test setup. Temperature and humidity controls shall be available wherever necessary during testing of samples. | Please confirm the min. size , layout of budling and share tender drawing for same. Also confirm the min. technical requirements in terms of building design and material. | Technical-Civil | Refer Amendment 01.

## Amendment-1
Tender No : SECI/C&P/PMC/11/0003/2021-22
The Design, Engineering, Supply, Construction, Erection, Testing & Commissioning of 100 MW (AC) Floating Solar PV Project having 10 years plant O&M
S. No. | Section | Page No. | Clause | Original Version | Amendment
1 | General | - | - | - | The Operation and Maintenance Period for the tender has been reduced from 10 (Ten) years to 05 (Five) years. This revised Operation and Maintenance Period of 05 (Five) years shall supersede the earlier O&M period of 10 years at all respective places in the RfB, wherever mentioned.
2 | RfS Title | - | - | The Design, Engineering, Supply, Construction, Erection, Testing & Commissioning of 100 MW (AC) Floating Solar PV Project having 10 years plant O&M | The Design, Engineering, Supply, Construction, Erection, Testing & Commissioning of 100 MW (AC) Floating Solar PV Project having 5 years plant O&M
3 | Section II - Bid Data Sheet | 49 | ITB 17 | (e) Comprehensive Operation & Maintenance (O&M) charges for total 10 years period shall be quoted in Schedule No 5/SOR 5.” | (e) Comprehensive Operation & Maintenance (O&M) charges for total 05 years period shall be quoted in Schedule No 5/SOR 5.”
4 | Section III - Evaluation and Qualification Criteria | 61 | Evaluation of Bids | ii. NPV of O&M for total 10 years i.e., Schedule No 5/SOR 5 including • Net Present Value (NPV) of O&M Price excluding GST/Taxation for the 10 years O&M period for the plant facilities to be calculated at a discounting rate as per Price Schedule No 5/SOR 5. Discounting Rate for NPV calculation considered is 8.30% | ii. NPV of O&M for total 5 years i.e., Schedule No 5/SOR 5 including • Net Present Value (NPV) of O&M Price excluding GST/Taxation for the 5 years O&M period for the plant facilities to be calculated at a discounting rate as per Price Schedule No 5/SOR 5. Discounting Rate for NPV calculation considered is 8.30%
5 | Section III - Evaluation and Qualification Criteria | 64 | Evaluation of Bids | 5. Schedule No 5: • The price evaluation for Schedule 5 will be done based on the NPV of O&M price excluding GST mentioned under CELL NO J 25. However, For the Purpose of Contract award, the total price mentioned under CELL No H 25 including Total O&M price of 10 years + GST will be considered from Schedule No 5. | 5. Schedule No 5: • The price evaluation for Schedule 5 will be done based on the NPV of O&M price excluding GST mentioned under CELL NO J 20. However, For the Purpose of Contract award, the total price mentioned under CELL No H 20 including Total O&M price of 5 years + GST will be considered from Schedule No 5.
6 | Section III - Evaluation and Qualification Criteria | 73 | 3.2 Average Annual Turnover | Minimum average annual turnover of INR 228 Crores (Indian Rupees Two hundred & Twenty-Eight Crores only) or USD 27 M (US Dollars Twenty-Seven Million only), calculated as total certified payments received for contracts in progress or completed within the last 03 (Three) years For Indian companies, other income (as per the Companies Act, 2013 including amendment/ clarifications), shall not be considered for arriving at annual turnover | Minimum average annual turnover of INR 223 Crores (Indian Rupees Two hundred & Twenty-Three Crores only) or USD 27 M (US Dollars Twenty-Seven Million only), calculated as total certified payments received for contracts in progress or completed within the last 03 (Three) years For Indian companies, other income (as per the Companies Act, 2013 including amendment/ clarifications), shall not be considered for arriving at annual turnover
7 | Section III - Evaluation and Qualification Criteria | 74 | 3.3 Financial Resources | The Bidder must demonstrate access to, or availability of, financial resources such as liquid assets & lines of credit, other than any contractual advance payments to meet: (i) the following cash-flow requirement: INR 95 Crores (Indian Rupees Ninety-Five Crores only) or USD 11 M (US Dollars Eleven Million only) | The Bidder must demonstrate access to, or availability of, financial resources such as liquid assets & lines of credit, other than any contractual advance payments to meet: (i) the following cash-flow requirement: INR 93 Crores (Indian Rupees Ninety-Three Crores only) or USD 11 M (US Dollars Eleven Million only)
8 | Section III - Evaluation and Qualification Criteria | 74 | - | General Clause | Lead Member/partner is the Lead Member or the Lead partner of the JV
9 | Section IX - Particular Conditions of Contract | 315 | PCC 8. Time for Commencement and Completion | PCC 8.2 The Time for Completion of the whole of the Plant Facilities shall be 18 (Eighteen) Months till commissioning from the Effective Date as described in the Contract Agreement or NTP, whichever is later. And Operation & Maintenance (O&M) of the Plant facility for a period of 10 (Ten) years from the date of Operational acceptance of the Plant Facilities. Complete Operation & Maintenance of the Plant Facilities is part of this contract. The scope of work, service level agreement and specific payment for O&M is consolidated and appended as “Appendix B” to the bidding document as “Part of Operations and Maintenance Agreement For the 100 MW AC Floating Solar PV Plant. | PCC 8.2 The Time for Completion of the whole of the Plant Facilities shall be 18 (Eighteen) Months till commissioning from the Effective Date as described in the Contract Agreement or NTP, whichever is later. And Operation & Maintenance (O&M) of the Plant facility for a period of 5 (Five) years from the date of Operational acceptance of the Plant Facilities. Complete Operation & Maintenance of the Plant Facilities is part of this contract. The scope of work, service level agreement and specific payment for O&M is consolidated and appended as “Appendix B” to the bidding document as “Part of Operations and Maintenance Agreement For the 100 MW AC Floating Solar PV Plant.
10 | Section IX - Particular Conditions of Contract | 318 | PCC 13. Securities | Second Stage: The value of the Contract Performance Security shall be 5% (Five) of the Contract Value {i.e. total sum of the Supply (Abroad & Employer’s country) & Service (Freight, Design, Installation & Civil Works) starting from the Operational Acceptance of the Plant Facilities, valid till the end of 10th year of the O&M period. Contractor needs to furnish the revised Contract Performance Security in the Second Stage amounting to 5% of the total Contract Value as mentioned above within the validity period of the Contract Performance Security submitted at First Stage. The contractor also has the option of the reduction of the Performance Security submitted at the First stage @ 10% to 5%, which is required to be submitted at Second Stage, within the validity period of the Contract Performance Security submitted at First Stage. In case of extension of the Operational Acceptance, the validity of the Performance Security will be extended suitably. The Performance Security may also be submitted in the form of Insurance Surety Bonds. Envisaging the difficulty in obtaining the longer tenure of CPS in the form of BG, the successful bidder can submit Contract Performance Security in the form of Bank Guarantee with initial validity period of 36 Months and the same may be extended for the balance period or further 36 months, within 60 days of expiry of the original CPS. ........ Contract Performance Security submitted at the Second Stage shall be released to the Contractor without any interest not later than 75 (Seventy-Five) days after the successful completion of the complete O&M period (10 Years) subject to the approval and acceptance of the O&M period deliverables by the Engineer in charge/Technical Team. | Second Stage: The value of the Contract Performance Security shall be 5% (Five) of the Contract Value {i.e. total sum of the Supply (Abroad & Employer’s country) & Service (Freight, Design, Installation & Civil Works) starting from the Operational Acceptance of the Plant Facilities, valid till the end of 5th year of the O&M period. Contractor needs to furnish the revised Contract Performance Security in the Second Stage amounting to 5% of the total Contract Value as mentioned above within the validity period of the Contract Performance Security submitted at First Stage. The contractor also has the option of the reduction of the Performance Security submitted at the First stage @ 10% to 5%, which is required to be submitted at Second Stage, within the validity period of the Contract Performance Security submitted at First Stage. In case of extension of the Operational Acceptance, the validity of the Performance Security will be extended suitably. The Performance Security may also be submitted in the form of Insurance Surety Bonds. Envisaging the difficulty in obtaining the longer tenure of CPS in the form of BG, the successful bidder can submit Contract Performance Security in the form of Bank Guarantee with initial validity period of 36 Months and the same may be extended for the balance period or further 36 months, within 60 days of expiry of the original CPS. ........ Contract Performance Security submitted at the Second Stage shall be released to the Contractor without any interest not later than 75 (Seventy-Five) days after the successful completion of the complete O&M period (05 Years) subject to the approval and acceptance of the O&M period deliverables by the Engineer in charge/Technical Team.
11 | Appendix A to Section VII, Chapter – 3: Special Technical Conditions | 168 of 309 | Cl. No. 3. Specific Requirements; Sl. No. 2 | Maximum block size for the FSPV plant shall not be higher than 4 MW (AC). Blocks shall be symmetrical in shape. | Maximum block size for the FSPV plant shall not be higher than 5 MW (AC). Blocks shall be symmetrical in shape.
12 | Appendix A to Section VII, Chapter 2: Technical Specifications, C: Civil Works | 158 of 309 | 28.11 | All fasteners used in the floating system shall be made of SS 316. | Void.
13 | Appendix A to Section VII, Chapter 2: Technical Specifications, C: Civil Works | 159 of 309 | 28.22.1 | The floating platform shall be made of HDPE/FRP or precast or cast in-situ fixed platform and shall be of adequate size for installation of equipment, associated facilities, movement and working of O&M personnel, etc. | The floating platform shall be made of HDPE/FRP/Stainless Steel(SS316)/precast or cast in-situ RCC/ferro cement fixed platform and shall be of adequate size for installation of equipment, associated facilities, movement and working of O&M personnel, etc.
14 | Appendix A to Section VII, Chapter 2: Technical Specifications, C: Civil Works | 148 of 309 | 13.6 | Reinforcement steel shall be of high strength TMT bars of grade Fe500 D conforming to IS: 1786 with anti-corrosive coating to withstand aqueous environment. Ductile detailing in accordance with IS: 13920 shall be adopted for all RCC buildings. | Reinforcement steel shall be of high strength TMT bars of grade Fe500 D conforming to IS: 1786. For offshore structures, reinforcements shall be provided with anti-corrosive coating to withstand aqueous environment. Ductile detailing in accordance with IS: 13920 shall be adopted for all RCC buildings.
15 | Appendix A to Section VII, Chapter 2: Technical Specifications, C: Civil Works | 153 of 309 | 25.6.1 | The fencing shall be of galvanized iron chain link mesh fabric with internal, corner and stay posts of hot dipped GI angle (min. ISA 65x65x6 mm) with 100mm thick M15 PCC foundation (min. width 450mm and min. depth 450 mm below GL). | The fencing shall be of galvanized iron chain link mesh fabric with internal, corner and stay posts of hot dipped GI angle (min. ISA 65x65x6 mm), as applicable, along with 230 thick brick/300 thick RR masonry toe wall, with 100mm thick M15 PCC foundation (min. width 450mm and min. depth 450mm below GL). Toe wall shall project minimum 150mm above ground level.
16 | Appendix A to Section VII, Chapter 2: Technical Specifications, C: Civil Works | 162 of 309 | 3.1 | The contractor shall make necessary provisions to provide all facilities required for QA & QC activities by setting up a field laboratory for QA and QC activities in line with the indicative field QA & QC laboratory set-up. | The contractor shall make necessary provisions to provide all facilities required for QA & QC activities by setting up a field laboratory (portable cabin type) for QA and QC activities in line with the indicative field QA & QC laboratory set-up. The min clear size for the portable cabin shall be 4.5 m x 3.0 m x 2.7 m. The foundation/support structure shall be as per manufacturer's recommendations. Other specifications for the portable cabin shall be same as specified for Security room (Cl. 29.3 under Civil Works Section of Chapter 2:Technical Specifications).
17 | Appendix A to Section VII, Chapter 1: Scope of Works |  | 6.25 | New Clause | Contractor shall supply and erect Site Office for Owner and test laboratory (both portable Cabin type). The min clear size for these facilities shall be 4.5 m x 3.0 m x 2.7 m. The foundation/support structure shall be as per manufacturer's recommendations. Other specifications for these shall be same as specified for Security room (Cl. 29.3 under Civil Works Section of Chapter 2:Technical Specifications).
18 | Appendix A to Section VII, Chapter 2: Technical Specifications, C: Civil Works |  | 30 | New Clause | Specifications for surface/area drainage : Refer Annexure N-Details of Recharge Pit for rain water harvesting.
19 | Appendix A to Section VII, Chapter 2: Technical Specifications, C: Civil Works | 158 of 309 | 28.1 | All the modules shall be accessible for maintenance once multiple floating units are connected together. | All the modules shall be accessible for maintenance once multiple floating units are connected together. Walkways have to be provided after every four rows of modules.
20 | Special Technical Specifications |  | 1 | S. No. 6 | Temperature details: Max Temp - 40.3 Deg C Min Temp - 6 Deg C Avg Temp - 24 Deg C
21 | Appendix A to Section VII, Chapter 1: Scope of Works | 16 of 309 | 6.8 | Construction of outdoor storage shed of area sufficient enough to store spares. | Construction of outdoor storage shed of area sufficient enough to store spares. Specifications for the same shall be as per Security room (Cl. 29.3 under Civil Works Section of Chapter 2:Technical Specifications). However, area shall be considered as per the project requirements.
22 | Appendix A to Section VII, Chapter 1: Scope of Works | 17 of 309 | 6.23 | Construction of approach path (RCC/Steel framed structure) to facilitate movement of personnel and equipment from the reservoir bank to the floating platform provided for access to the boat/vessel. This floating platform shall be located where adequate water depth is met at MDDL for the movement of boat/vessel and shall be suitably anchored. | Construction of approach path (RCC/Steel framed structure) to facilitate movement of personnel and equipment from the reservoir bank to the floating platform located adjacent to the reservoir bank. This floating platform shall be provided for access to the boat/vessel and shall be located where adequate water depth for the movement of boat/vessel is met at MDDL condition. The platform shall be suitably anchored/moored.
23 | Appendix A to Section VII, Chapter 2: Technical Specifications, B: Electrical Works | 81 of 309 | 10.8.4 | Off Shore In case of string inverter, AC cables from inverter to AC Combiner Panel shall be laid through UV resistant Double Wall Corrugated HDPE conduits. The size of the conduits shall be selected on the basis of 40% fill criteria. The conduits shall be routed through closed cable trays fixed on top of the floats on the PV Module floating platform. The conduits shall be routed on top of dedicated floats (on-shore) from PV Module floating platform through appropriate support structure till transformer. Conduits shall be tied to the cable trays at regular intervals using UV resistant cable ties. | Off Shore AC cables shall be laid over cable trays fixed to floating platform and tied with UV resistant cable ties. Cables from PV Module floating platform to transformer platform shall be routed through appropriate structure on top of dedicated floats.
24 | Appendix A to Section VII, Chapter 2: Technical Specifications, C: Civil Works |  | 11.11 | New clause | For the design of floats and module support structures, no reduction in design wind pressure shall be considered. However, for the design of anchoring and mooring system 20% reduction in the design wind pressure may be considered.
25 | Appendix A to Section VII, Chapter 2: Technical Specifications, C: Civil Works | 154 of 309 | 26.4 | As the ground water at site may not be suitable for construction and module cleaning purposes. Suitable water for construction and module cleaning purposes (during plant operation) by providing RO plant of requisite capacity including storage facilities shall be arranged by the bidder. | Suitable water for construction and module cleaning purposes (during plant operation) by providing RO plant of requisite capacity including storage facilities shall be arranged by the bidder.
26 | Appendix A to Section VII, Chapter 1: Scope of Works | 17 of 309 | 6.18 | Construction of storm water drainage & sewage network including rain water harvesting mechanism (on-shore). | Construction of storm water drainage & sewage network including rain water harvesting mechanism (on-shore). Rain water harvesting system (min 01 No.) shall be of Recharge pit type. Refer Annexure N: Details of Recharge Pit for rain water harvesting to the Technical Specifications.
27 | Appendix A to Section VII, Chapter 2: Technical Specifications, Annexure A: PV Module Pre-dispatch Inspection Protocol | Page-174 of 309 | 6. Sampling Process: | c. Same samples shall be used for all Witness Tests stated at 5.2 above. | c. Same samples shall be used for all Witness Tests stated at 5 above.
28 |  | Page 217 of 309 | 3.1.2 General Requirements before Starting the Commissioning Process | Electroluminescence camera, power supply and accessories | Void.
29 | Appendix A to Section VII, Chapter 1: Scope of Works | 13 | 4.27 | Weather monitoring station shall include but not be limited to the following  Pyranometers – Two in Horizontal Plane for GHI and two in inclined plane for GTI – Minimum 4 (Four) Nos.  Ultrasonic Anemometer (wind speed and direction) – 2 (two) no.  Temperature Sensor (ambient and module surface) – 3 (three) nos.  Power source to the all sensors wherever required  Data Logger | Weather monitoring station (Three Nos.) shall include but not be limited to…....
30 | Appendix A to Section VII, Chapter-2 : Technical Specification | pdf page No. 67 of 309 | 8.3.3 | The panel enclosure shall be constructed with CRCA steel/Aluzinc sheet. The thickness of load bearing members shall be minimum 3 mm and that of non-load bearing members shall be minimum 2 mm. | The panel enclosure shall be constructed with CRCA steel/Aluzinc sheet. The thickness of load bearing members shall be minimum 3 mm and that of non-load bearing members shall be minimum 2 mm or as per OEM design with Type Test Reports.
31 | Appendix A to Section VII, Chapter 2: Technical Specifications, Annexure A | Page-174 of 309 | 6. Sampling Process: | Note: Smallest lot size for Inspection: 20% of the capacity as per the PO. | Note: Smallest lot size for Inspection: 10 MW
32 | Appendix A to Section VII, Chapter 2: Technical Specifications, C: Civil Works | Page-174 of 309 | 28.21 | Warranty: The Floating System including floats, mooring and anchoring mechanism shall be warranted for 10 years. | Warranty: The Floating System including floats, mooring and anchoring mechanism shall be warranted for 5 years.
33 | Appendix A to Section VII, Chapter 2: Technical Specifications, Annexure G - O&M Agreement, Annexure 2: Functional Guarantees | Page-281 of 309 | C | DF is module degradation factor, 0.5% per year | DF is module degradation factor, as per approved OEM datasheet.
34 | Standard Procurement Document, Appendix 8. Functional Guarantees. | Page 355 of 365 | 2. D. | Liquidated Damages for Shortfall in Annual CUF for Solar PV Plant …... | Liquidated Damages for Shortfall in Annual CUF for Solar PV Plant - Please refer Annexure G: Plant Operation & Maintenance Agreement of 100 MW (AC) Floating Solar PV Project at Getalsud Dam, Ranchi.
35 | Appendix A to Section VII | - | - | - | Annexure-H- Reservoir Details and Drawings Annexure-I Available Reservoir Area with Contour Details Annexure J - Borehole Locations and Logs Annexure-K - Tender Drawings Annexure L - Tentative Route Map for Transmission Line Annexure M: ESIA Scope of Works Annexure N-Details of Recharge Pit for rain water harvesting. Annexure O - Plan & Section of Cable Crossing Annexure P - Approved FOTE Specifications - GA, GTP, BOQ, Layout and Scheme Drawings Annexure Q - SLD of 132/33 kV Irba Grid Substation
36 | Price Schedule | - | - | - | Updated Price Schedule is attached separately with Amendment 01.
37 | New Document | - | - | Resettlement Action Plan (RAP) | Resettlement Action Plan (RAP) is attached separately with Amendment 01 for Compliance & Adherence which forms an integral part of the RfB.