## Pre Bid Clarifications
Tender No. SECI/C&P/OP/11/0006/2022-23 Dated: 13/04/2023
DESIGN, ENGINEERING, SUPPLY (EXCEPT PV MODULES), CONSTRUCTION, ERECTION, TESTING & COMMISSIONING OF 300 MW (AC) GROUND MOUNTED Ramagiri, Andhra Pradesh
Sl. No. | Tender Section | Page No. | Clause | Description as per Bidding Document | Queries | Category | Clarifications
1 | SPECIAL CONDITIONS OF CONTRACT | 155 of 219 | 1 | Construction Water: To be arranged by the Contractor | It is requested to provide Construction water and Construction Power to the Bidder | Technical | The terms and conditions of the tender document shall prevail.
2 | SPECIAL CONDITIONS OF CONTRACT | 155 of 219 | 1 | Construction Power: To be arranged by the Contractor |  | Technical
3 | SECTION-VII: SCOPE OF WORKS | 17-18 of 329 | 7.2 | All statutory approvals / permissions and/or No Objection Certificates (NoC) etc. from DISCOM / STU / CTU for interconnection of solar power plant at the substation. | Being SECI Owner/Employer of the project, all statutory approvals/permissions and/or No objection certificate from DISCOM shall be arranged by SECI. Kindly confirm. This is also necessary for timely commissioning of the project | Technical | The terms and conditions of the tender document shall prevail.
4 | SECTION-VII: SCOPE OF WORKS | 18 of 329 | 7.6 | All other statutory approvals and permissions and their respective compliances, not mentioned specifically but are required to carry out hassle free Construction and O&M of the plant. | Being SECI Owner/Employer of the project, It is requested to Kindly consider that all the statutory approvals except CEIG shall be in the scope of SECI. Kindly consider. | Technical | The terms and conditions of the tender document shall prevail.
5 | SECTION - VII B. TECHNICAL SPECIFICATIONS | 31 of 329 | 3.2.1 | The Inverter Supplier should have supplied minimum 5 GW capacity globally or 500 MW in India in the past 5 years | Kindly waive off this requirement as this will restrict the Inverter suppliers. | Technical | The terms and conditions of the tender document shall prevail.
6 | SECTION - VII B. TECHNICAL SPECIFICATIONS | 109 of 329 | 25.2 | The Contractor shall get the route approval from the Employer prior to start of the construction. Any changes in the route or scheme due to ROW issues at any point of the time prior to commissioning shall be complied without any additional cost to the Employer. | Route approval may be provided by SECI to bidders in order to firm up the transmission line estimate. | Technical | The Contractor shall submit transmission line route for the approval of the Employer during detailed engineering stage. For the purpose of estimation, approximate transmission length has been specified in the tender document. The terms and conditions of the tender document shall prevail.
7 | SECTION - VII A. SCOPE OF WORKS | 5 of 329 | 1, Project Particulars | Module Mounting Structure Type: East-West Fixed Tilt (Tilt angle: 5°) | The clauses are contradictory in nature. Kindly confirm whether the tilt angle is fixed at 5° or at 5°-15° | Technical | Please refer S.No.1 of Amendment-1. The MMS is fixed tilt type. However, the tilt at which the modules are fixed depends upon the ground slope. As the ground slope varies from 0-5° in E-W direction, tilt of the module w.r.t. the horizontal varies from 5-15°. This shall be achieved by rotating the rafter to the required inclination while setting up the MMS. Kindly refer MMS drawing attached in Annexure-D including notes for further clarification.
8 | SECTION - VII A. SCOPE OF WORKS; 6 Civil Works | 15 of 329 | 6.6.1 | MMS shall be fixed tilt, double slope, free standing canopy structure in E-W configuration with tilt of 5°-15° |  | Technical
9 | SECTION - VII A. SCOPE OF WORKS; 6 Civil Works | 17 of 329 | 6.2 | Suitable arrangement of water shall be ensured to cater to day-to-day requirement of drinking water and permanent water supply for module cleaning and other needs of SPV power plant during entire O&M period. | It is requested to Kindly consider the water charges during O&M in the scope of Employer. | Technical | The terms and conditions of the tender document shall prevail.
10 |  | 149 OF 329 |  | MODULE CLEANING SYSTEM :::: PLS CHECK | In case the Bidders opts for water cleaning, then SECI is requested to provide water connection for the same during the construction period and O&M period. | Technical | The terms and conditions of the tender document shall prevail.
11 | BID DATA SHEETS (BDS); SL NO. 6 | 63 of 219 | 19.1 | The bid validity period shall be 180 (One Hundred and Eighty Days) from the date of opening of Techno-Commercial Bid (Envelope-I). | Owing to still prevalent volatility in commodity prices, OEMs are not giving the long term price validity, hence it is requested to Kindly consider the bid validity as 90 days. | Contractual | The terms and conditions of the tender document shall prevail.
12 | SECTION - II INSTRUCTION TO BIDDERS (ITB) | 28 of 219 | 13.6 | Owner will reimburse the GST to the Contractor at actuals against documentary evidence subject to the ceiling amount of GST as quoted by the bidder, subject to any statutory variations. In case of any variation in the executed quantities (If directed and/ or certified by the Engineer-In-Charge) the ceiling amount on which GST is applicable will be modified on pro-rata basis. | It is requested to kindly re-imburse the GST at actuals under the change in law clause without the ceiling limit. Further this is in contrary to the GCC Clause No. 36.1 regarding Change in Law. | Contractual | The purpose of this very clause is to exercise utmost diligence by the bidders while filling the taxation/GST part. There may be situations wherein bidder may wrongly quote a irrelevant GST though the actual applicable GST is more. As the evaluation is inclusive of taxes so the GST/taxation part cannot be changed post award which is primarily due to bidders mistake. Further there is no contradiction found in this particular clause and the GCC Change in Law clause.
13 | SPECIAL CONDITIONS OF CONTRACT (SCC) | 153 of 219 | Sl No. 3 | The Time for Commissioning for the cumulative capacity of 300 MW Ground mounted Solar PV Power Plant at Ramagiri along with other associated equipment as per this tender document in total shall be 12 (Twelve) Months from the Date of the Notification of Award NOA/LOA/LOIN. | Considering the size of Solar project and transmission line it is requested to Kindly consider the time for commissioning as at least 18 months from the handing over of site. Kindly accept. | Contractual | Kindly refer S.No. 48 and S.No. 49 of Amendment-1.
14 | GENERAL CONDITIONS OF CONTRACT (GCC) | 81 of 219 | 1.1.32 | EFFECTIVE DATE means the date of issuance of Notification of Award/ Letter of Intent/Letter of Award (LOA). | It is requested to Kindly consider the effective date as the date of handing over of encumbrance free land. Kindly accept. It is gathered from the site visit that a parcel of Private land of around 5.86 acres is enclaved in the Plot B1 . It is requested to clarify whether the Private land has to be fenced by the BoS Contractor. Also what kind of and from where approach has to be provided to the Private land Also, SECI is requested to clarify whether the public road between Plot B1 and B2 has to be fenced and enclosed or it is to be left open for public use. | Technical | Effective Date for issuance of Notification of Award/ Letter of Intent/Letter of Award (LOA) shall be as per the terms and conditions of the tender document. Any fencing if required for private land will be in the scope of Contractor. And further fencing will be required for the entire Solar Power Plant.
15 | General |  |  | Monthly Reference Radiation | It is requested to Kindly share the reference radiation which to be considered by bidders. | Technical | Solargis TMY (01/01/1999 to 31/12/2021) file has been used for energy yield estimation. The bidder may use the same for bidding. However, it shall be noted that radiation correction will be done based on annual radiation only.
16 | GCC | 93 of 219 | 19 | Force Majeure | It is requested to Kindly consider the Pandemic, epidemic, Lockdown etc as Force Majeure. Kindly accept. | Contractual | Kindly refer S.No. 47 of Amendment-1.
17 | GCC | 144 of 219 | 100 | Disputes and Arbitration | As per the Office Memorandum (OM) dated 22.05.2018 of Ministry of Heavy Industries & Public Enterprises (F.No. 4(1)/2013-DPE(GM)/FTS-1835), which has been marked to Chief Secretary of all states, whereby disputes or differences between Central Public Sector Enterprise (CPSE) and state government Department/ Organization relating to the interpretation and application of the provisions of commercial contract(s), shall be taken up for resolution through AMRCD. Kindly confirm. | Contractual | The terms and conditions of the tender document shall prevail.
18 | SPECIAL CONDITIONS OF CONTRACT (SCC) | 156 of 219 | 13 | First Stage (Supply and Services): The value of the Contract Performance Security shall be 3% (Three percent) of the Contract Value (i.e., total sum of the Supply & Service Contract). This Performance security will be valid for a total period of 75 Months (12 Months Project commissioning period) + prescribed O & M Period, i.e., 60 Months + 03 Months additional) from the date of its issuance. | It is requested to kindly consider that the Performance security during O&M as 3 % of O&M contract Price instead of EPC Price. Kindly accept. Reduction in the PBG during O&M could be done after the beginning of the O&M period which we proposed should begin after the successful commissioning of the plant i.e. synchronisation to the grid | Contractual | Kindly refer S.No. 50 of Amendment-1.
19 | SECTION - II INSTRUCTION TO BIDDERS (ITB) | 31 of 219 | 20 | E-PAYMENT | It is requested to Kindly consider the release of payment through irrevocable Letter of Credit payable at sight. | Contractual | The terms and conditions of the tender document shall prevail.
20 | SECTION - VII A. SCOPE OF WORKS | 7 of 329 | 3.2 | All documents and drawings (soft copy) shall be submitted to the Employer for review and approval. Every drawing shall also be submitted in ‘*.dwg’ format. In case of design calculations done in spread sheet, editable (working) soft copy of the spread sheet shall also be submitted along with ‘pdf’ copies during every submission. | The submission of drawing in hard copies before approval in cat-I is to be reviewed. All soft copies of the documents and drawings shall be uploaded on an online platform for the seamless review of customer. Also there can be multiple revisions for approval. The final approved set of drawings shall be submitted in hard copy. | Technical | Kindly refer Line 6 of Clause 3.2 of Scope of Works. "Five nos. of hard copies of approved documents and drawings shall be submitted to the Employer." Hard copies are required only for approved drawings. The terms and conditions of the tender document shall prevail.
21 | SPECIAL CONDITIONS OF CONTRACT (SCC) | 155 of 219 | 4 | Cutting of trees, bushes and vegetation from site (including permission from local authorities) and disposal thereof. The site should be maintained in vegetation free condition during erection stage (at any point of time) i.e., up to start of O&M Contract. | The cutting/removing of trees/bushes etc. shall be insc scope of the BoS contractor . However, SECI is requested to arrange the approvals of the same. | Contractual | Any approval if at all required during the process of cutting/removal of trees/bushes will be facilitated by SECI.
22 | SPECIAL CONDITIONS OF CONTRACT (SCC) | 159 of 219 | 13 | All PV Modules supplied by the Owner at the site shall be inspected at site by the Contractor along with the Owner. In all cases necessary test certificates, guarantee certificate in respect of material/equipment performance shall be furnished by the Contractor. | Since PV modules are being supplied by SECI. This clause may be suitably modified. | Contractual | As it is a tri-party inspection of modules at site by Owner(SECI), Module Supplier and BoS Contractor, inspection of Modules at site will be in the scope of Contractor.
23 |  |  |  | General Query | Please provide KML file to know the exact location and boundary of the usable area. | Technical | The CAD file of tentative land layout attached in Annexure-C to Section-VII is geo-referenced. It can be exported to KML file.
24 | General |  |  |  | Liquidated Damages/Penalty shall not be imposed on contractor, if the delay is attributable to SECI. | Contractual | All such situation will be dealt on case to case basis, in line with the provision of the tender document.
25 | General |  |  |  | We request SECI to kindly consider the price and time implication due to change in law, regulation, ordinance, order as the Contractor will be bound to adhere any the change in law, regulation, ordinances and orders issued by government. | Contractual | The terms and conditions of the tender document shall prevail.
26 | General |  |  |  | If delay from scheduled completion is on account of employer, then any statutory variation beyond stipulated Delivery/ Commissioning/Completion schedule shall be to customer’s account. | Contractual | All such situation will be dealt on case to case basis, in line with the provision of the tender document.
27 | General |  |  |  | It is requested to kindly consider that no Liquidated Damages/Penalty shall be imposed on account of delay due to Force Majeure. | Contractual | All such situation will be dealt on case to case basis, in line with the provision of the tender document.
28 | General (regarding Delay not in scope of the BoS contractor like local disturbances, supply of PV modules ) |  |  |  | The delay in commissioning/completion due to external issues beyond the control of contractor shall not be in the account of Contractor. In case of delay in supply of PV modules from the specified schedule of 1st Sep 23 to 31st May 24, it is requested to specify in particular the commensurate time extension which shall be allowed to the BoS contractor In case of delay due to the local disturbance will not be in the account of contractor. Kindly accept and confirm. | Contractual | Exact timeline for the supply of Modules will be communicated to the successful bidder and smooth transition will be ensured by SECI between Module supply at site and BoS Contractor timeline.
29 | Section VII: TECHNICAL SPECIFICATIONS | 175 of 329 | Annexure-A (PG Test Procedure) | Liquidated Damages for Shortfall in PR: For every 0.01 shortfall in PR below the specified PR value, liquidated damages of 1% of the Contract Value shall be levied. In case the Plant PR Shortfall is more than 0.05 below the specified PR value, then the total plant will be accepted on “as-is basis” & no payments will be made to the contractor pertaining to ‘Operation Acceptance’ milestone in line with the defined payment terms. However, any other earlier pending/running payments as may be applicable, will be paid to the contractor as usual. | Since supply of Modules are not in the scope of BOS contractor, it is requested to not seek CUF & PR guarantees from the BOS contractor. In place of the same, an OTGT (O&M Target Guarantee Test) may be stipulated in line with the standard industry practice being followed by other PSUs viz. NTPC, SGEL etc. | Technical | Kindly refer S.No.5 and S.No.6 of Amendment-1. Specified PR and CUF will be adjusted for any shortfall due to module performance that is not attributable to the Contractor.
30 | Section VII: TECHNICAL SPECIFICATIONS | 318 of 329 | ANNEXURE 2 (D) | If the Contractor fails to achieve guaranteed annual CUF at the end of First Year, the Contractor shall pay compensation to the Employer (amount to be deducted from the Final Payment at the end of 1st year), an amount equal to the NPV of the estimated shortfall in cash flow resulting over the period of 25 years due to reduced Plant CUF, calculated at a tariff of Rs.2.57 per unit (kWh) and discount rate of 6.67%. |  |  | The terms and conditions of the tender document shall prevail.
31 | General |  |  | General Query | Kindly consider 3 years O&M instead of 5 years as per standard Industry practice being followed bby other PSUs viz. NTPC, SGEL etc. | Contractual | The terms and conditions of the tender document shall prevail.
32 | BID INFORMATION SHEET | 9/219 | A | ………. on turnkey basis at Ramagiri along with 5 (Five) years comprehensive operation and maintenance from the date of commissioning or Operational Acceptance, whichever is later. | We request to consider start of O&M from the date of Commissioning | Contractual | The terms and conditions of the tender document shall prevail.
33 | SECTION-VII: B: TECHNICAL SPECIFICATIONS | 109/329 | 25.3 | The ROW for the TL/UG cable shall be obtained prior to the construction of the line from the concerned authorities. | It is requested to either kindly consider the scope of ROW in the scope of Employer or completely exclude the scope of transmission line from the scope of contractor. Kindly accept and confirm. This is requested to ensure timely commissioning of the solar project In case the above is not acceptable it is requested to allow the scheduled time of the BoS contractor to begin only once all the approvals pertaining to the Project, Transmission line etc. are in place. | Technical | The terms and conditions of the tender document shall prevail.
34 | SECTION - IV GENERAL CONDITIONS OF CONTRACT | 104/219 | 32.1.2 | The Contractor shall acquire, on behalf of Owner, in the Owner’s name, all permits, approvals and/or licenses from all local, state or national government authorities or public service undertakings in the Country/State where the Site is located that are necessary for the setting up of the Plant & operation of Plant till its desired life as mentioned under the Contract, including, but not limited to, entry permits for all imported Owner’s/Employer's Equipment (if any). | We request to keep statutory approvals in SECI's scope In case the above is not acceptable it is requested to allow the scheduled time of the BoS contractor to begin only once all the approvals pertaining to the Project, Transmission line etc. are in place | Contractual | The terms and conditions of the tender document shall prevail.
35 | SECTION-VII: SCOPE OF WORKS | 17/329 | 7.1 | Obtaining statutory approvals /clearances/ compliances on behalf of the Employer from various Government Departments, not limited to, the following: • Pollution control board clearance, if required • Mining Department, if required • Forest Department, if required • All other approval as and when, as necessary for setting up of the solar power plant including CEIG/ CEA, power evacuation, etc. as per the suggested guidelines. | Being SECI Owner/Employer of the project, it is requested to Kindly consider the statutory approvals/clearances in the scope of SECI . However, contractor will provide the necessary support for obtaining the approvals. CEIG approval shall be taken by contractor. | Technical | The terms and conditions of the tender document shall prevail.
36 | SPECIAL CONDITIONS OF CONTRACT (SCC) | 160/219 | Schedule of Rates & Payments (GCC clause 80.1) | Seventy percent (70%) payments shall be paid on Pro rata basis against supply, receipt and acceptance of Materials at site……………………………….. | We request 70% payment on pro rata basis against dispatch of material | Contractual | The terms and conditions of the tender document shall prevail.
37 | BID INFORMATION SHEET | 10/219 | (A) 1.12 | Obtaining all associated statutory and regulatory compliances and approvals for successful construction, commissioning and operation of plant | We request to keep all approvals in SECI's scope In case the above is not acceptable it is requested to allow the scheduled time of the BoS contractor to begin only once all the approvals pertaining to the Project, Transmission line etc. are in place | Contractual | The terms and conditions of the tender document shall prevail.
38 | SOW | Page 4 of 20 | 1 Project Particulars | Transmission Line from Pooling Substation to Interconnecting Substation | Customer is requested to please provide the specification for the Transmission Line to be followed. | Technical | Kindly refer Clause 4.15 of Scope of Works. 220 kV Transmission Line / Underground Cable shall be as per the specifications of CTU.
39 | SOW | Page 4 of 20 | 1 Project Particulars | Transmission Line from Pooling Substation to Interconnecting Substation | Customer is requested to please provide a tentative corridor/route for the Transmission Line , so that the number of towers be worked out . | Technical | Assessment of transmission line route from Plant Pooling Substation to Interconnecting Substation is in the scope of the Contractor. For the purpose of estimation, approximate transmission length (18 km) has been specified in the tender document.
40 | SOW | Page 6 of 20 | Design and Engineering Clause 3.3 | Design calculations and sheets (licenced software as well as design templates | Supply of Design Software's for 220kV S/s is not considered in the scope of the BIDDER. Please Clarify | Technical | Kindly refer S.No.7 of Amendment-1.
41 | SOW |  | Annexure – C | Annexure – C Tentative Land Layout with Contour Details | Please provide the GPS Coordinate of the Site . Also kindly provide the Khasra No of the Land envisage for the 220kV Switchyard | Technical | The CAD file of tentative land layout attached in Annexure-C to Section-VII contains UTM coordinates. Exact location of 220 kV Plant Pooling Substation shall be decided during detailed engineering.
42 | SOW |  | Annexure – C | Annexure – C Tentative Land Layout with Contour Details | Customer is requested to please share the SLD of 220kV System. | Technical | The design parameters of 220 kV Plant Pooling Substation (Quantity of 33/220 kV Transformers, Switching Scheme, No. of circuits in 220 kV transmission line) required for development of SLD are provided in Clause 1 of Scope of Works.
43 | SOW | Page 42 of 143 | TS | 11.7 Switchyard Earthing The metallic frame work of all switchyard equipment and support structures shall be connected to the earth grid by means of two separate and distinct connections. | The Grounding system for 220kV System shall be made up of MS Rod and GS Flat | Technical | Kindly refer S.No.20 of Amendment-1.
44 | SOW | Page 43 of 143 | TS | 12 . Lightning Protection System Protection level for the entire plant shall be Level-III. | IS / IEEE may also be accepted along with IEC for the Lightning Protection . Please confirm | Technical | As mentioned in Clause 12.1 of Technical Specifications, Lightning Protection System (LPS) for the entire plant except plant pooling substation against direct lighting strokes shall be provided as per IS/IEC 62305:2010.
45 | SOW | Page 63 of 143 | TS | Rated short-time withstand current 40 kA or 50 kA for 1 s (as applicable) | Rated Short Circuit evel may please be specified .Requesting to please confirm the short circuit requirement of the 220kV Substation | Technical | Kindly refer S.No.24 of Amendment-1.
46 | TS | Page 64 of 143 | 19.4.1 Technical Parameters | No. of contacts As required plus 10 NO and 10 NC contacts per pole as spare | The NO and NC Contacts shall be provided as per the Manufacturer design | Technical | The terms and conditions of the tender document shall prevail.
47 | TS | Page 64 of 143 | 19.4.1 Technical Parameters | 5 Area Grading and Land Development | Please inform the FGL Level for the 220kV Substation . | Technical | It shall be decided during detail engineering.
48 | Schedule No. 3. Operation & Maintenance |  | Schedule No. 3. Operation & Maintenance | O & M Charges on YoY basis must be in equal or in ascending order only. | We request to kindly remove this requirement. Please Clarify | Contractual | The terms and conditions of the tender document shall prevail.
49 | VII-A | 317 | Annexure-2 | Reference Irradiation for the site = 2008 kWh/m2 | Please provide monthly irradiation values for energy estimation | Technical | Solargis TMY (01/01/1999 to 31/12/2021) file has been used for energy yield estimation. The bidder may use the same for bidding. However, it shall be noted that radiation correction will be done based on annual radiation only.
50 | VII-A | 6 | Project Particulars | Performance Parameters: Performance Ratio at 220 kV side of Plant Pooling Substation 85.90%, Capacity Utilization Factor at 220 kV side of Interconnecting Substation - 21.66% | Energy generation of solar PV plant majorly depends on performance and quality of PV modules. As the PV modules are supplied by owner, it is not possible to guarantee PR and CUF by EPC contractor. Request you to amend the clause so that EPC guarantee will be to guarantee the generation will be finalized after commissioning and PG test of the plant (Also called as O&M target generation test/ OTGT). This is being followed by other PSUs like NTPC and SJVN where modules are being supplied by owners. | Technical | Kindly refer S.No.5 and S.No.6 of Amendment-1. Specified PR and CUF will be adjusted for any shortfall due to module performance that is not attributable to the Contractor.
51 | VII-A | 6 | Project Particulars | Performance Ratio at 220 kV side of Plant Pooling Substation 85.90%, | Performance ratio requirement is very high compared t industry standard even with thin-film PV modules. Based on the PAN file provided, the losses due to PV module (IAM factor on global, PV loss due to irradiance level and PV loss due to temperature) itself are coming to more than 10% and with other losses (soiling loss, DC cable losses, transformer losses for 33kV & 220kV, inverter loss, AC cable losses for LT & 33kV, auxiliary loss, system unavailability etc.) are also there. Hence, kindly review and reduce to 80 to 82%. | Technical | Kindly refer the formula of Performance Ratio mentioned in Clause 2.1.1 of Annexure-A (PG Test Procedure) to Section-VII. Performance Ratio is corrected to 25°C. Hence, temperature loss should not be accounted in the calculation of PR. The terms and conditions of the tender document shall prevail.
52 | VII-A | 5 | Project Particulars | Module Technology: Thin-film (520 Wp – 540 Wp) (Not in the scope of EPC Contractor) | Please confirm whether PV module wattage will vary from 520 to 540 or it will be 520Wp only as the PAN file is provided for 520Wp only | Technical | PV Module power rating will vary between 520 Wp and 540 Wp.
53 | VII | 325 | Annexure – J | PV Module PAN File | Please confirm whether the PAN file provided in tender document is final or will get changed later? | Technical | Yes
54 | VII-A | 10 | 4.15 | 220 kV Over Head Transmission Line / Under Ground Cable including Towers, Conductors, Insulators, Cable Termination Kits and associated accessories from 33/220 kV Pooling Substation to Interconnecting Substation as per CTU drawings/specifications including Right of Way, permits and approvals, CTU supervision and maintenance charges. | We request to consider construction of 220kV transmission line in scope of owner completely or exclude right of way from EPC contractor scope | Technical | The terms and conditions of the tender document shall prevail.
55 | VII-A | 10 | 4.16 | 220 kV bay at interconnecting substation as per CTU drawings/specifications including shifting or replacement of substation equipment / materials, permits and approvals, CTU supervision and maintenance charges. | We request to consider construction of 220kV bay in scope of owner | Technical | The terms and conditions of the tender document shall prevail.
56 | VII-A | 17 | 6.10 | Construction of storage area for storage of modules | Bidder proposes for ensuring continuous fixing of modules, hence storage area is not required. Kindly confirm. | Technical | Based on the delivery schedule of PV Modules by the Supplier (Kindly refer S.No.8 of Amendment-1) and installation plan by the EPC Contractor, quantum of storage area shall be decided.
57 | VII-A | 17 | 6.17 | Construction of approach roads, access roads, internal roads and peripheral roads, as applicable. | Approximate length of various types of roads to be shared. | Technical | Length of various types of roads depends on the plant layout which is in the scope of the Contractor.
58 | VII-A | 17 | 6.18 | Construction of storm water drainage network for smooth disposal of storm water from the plant to the nearest available drainage outlet | Type of drainage required to be specified. Whether earthen drain or Brick / PCC lined drain or RCC drain is required. Kindly confirm. | Technical | The Contractor is free to choose the type of drain from the alternatives laid down in Technical Specifications.
59 | VII-A | 17 | 6.18 | Construction of storm water drainage network for smooth disposal of storm water from the plant to the nearest available drainage outlet. | Bidder requests employer to furnish coordinates of multiple/single discharge | Technical | It shall be decided during detail engineering depending on the site topography.
60 | VII-A | 17 | 6.20 | Suitable arrangement of water shall be ensured to cater to day-to-day requirement of drinking water and permanent water supply for module cleaning and other needs of SPV power plant during entire O&M period | Bidder requests owner to arrange for water supply | Technical | The terms and conditions of the tender document shall prevail.
61 | VII-B | 110 | 1.4.2 | Design of concrete structures shall conform to IS: 456 and IS: 13920. | Bidder proposes design as per IS:456 only. | Technical | Kindly refer S.No.28 of Amendment-1.
62 | VII-B | 123 | 10.2 | Imposed (Live) Load | Bidder proposed imposed live loads as per relevant i.e. IS:875 | Technical | The terms and conditions of the tender document shall prevail.
63 | VII | 186 | ANNEXURE - D | CHAIN LINK FENCE DRAWING | 1. Bidder proposed fixing of chain-link fencing without horizontal angles (35x35x3) as mentioned. Alternatively brick work at the bottom is proposed to ensure anchoring of chain link fencing at bottom. 2. Bidder proposes for adopting ISA 50x50x6 post checking as per Design in place of ISA 75x75x6 post | Technical | The terms and conditions of the tender document shall prevail.
64 | VII-B | 135 | 14.3 | Cement higher than 43 Grade shall not be used in construction. | Bidder proposes to use PPC due to low availability of OPC-43 grade. Employer to confirm | Technical | The terms and conditions of the tender document shall prevail.
65 | VII-A | 12 | 5 | Installation, Testing and Commissioning - For Transmission line, Pooling Station etc. | Please confirm whether the O&M of the transmission line and pooling station is in Contractor's scope? | Technical | Yes the O&M of transmission line and polling station is in Contractor's scope.
66 | VII-A | 17 | 6.20 | Suitable arrangement of water shall be ensured to cater to day-to-day requirement of drinking water and permanent water supply for module cleaning and other needs of SPV power plant during entire O&M period. | Whether customer can provide the water? If yes, what will be the charges? What will be water source capacity? What is the nearest source of water availability? | Contractual | Kindly refer to GCC Clause 2.3 and SCC Clause 5 for information on the same.
67 | VII-A | 18 | 7.8 | The Contractor shall comply with the provision of all relevant acts of Central or State Governments including payment of Wages Act 1936, Minimum Wages Act 1948, Employer's Liability Act 1938, Workmen's Compensation Act 1923, Industrial Dispute Act 1947, Maturity Benefit Act 1961, Mines Act 1952, Employees State Insurance Act 1948, Contract Labour (Regulations & Abolishment) Act 1970, Electricity Act 2003, Grid Code, Metering Code, MNRE guidelines or any modification thereof or any other law relating whereto and rules made there under or amended from time to time. | What are the applicable minimum wages at site? Central or State | Contractual | Applicable State Wages.
68 | VII-A | 20 | 8.11 | Availability of vehicles for Employer staff during construction and O&M period as per requirement may be ensured, failing which Employer shall have full right for alternate arrangement at the risk & cost of the contractor. | Please provide following details regarding vehicles for Employer staff: Type of Vehicle? No. of Vehicle during O&M? Approximate running of vehicle in Km. per month? | Contractual | Kindly refer to GCC Clause 28 for information on the same.
69 | VII-A | 20 | 8.12 | The contractor shall be responsible for all the required activities for the successful running, committed energy generation & maintenance of the Solar Photovoltaic Power Plant covering: Periodic cleaning of solar modules as approved by the Employer and water quality as per the recommendations of OEM | What will be the frequency of dry & wet module cleaning in cycle per months? | Technical | As mentioned in Clause 6.19 of Scope of Works, only wet type module cleaning system is allowed. The frequency of cleaning shall be decided so as to meet the CUF guarantee mentioned in the tender document. The terms and conditions of the tender document shall prevail.
70 | VII | 40 of 329 | 4.6.1.3 | Auxiliary transformer energy efficiency shall correspond to 3-star BEE rating or better as per BIS guidelines. | Currently BEE star rating is available for oil filled transformers only. Hence 3-star rated efficiency can not be guaranteed. Losses and efficiency of the transformer will be quoted on the finalization of the rating. | Technical | Auxiliary transformer may be oil-filled or dry type. Kindly refer S.No.18 of Amendment-1.
71 | VII | 284 | Annexure – I, 2.2.4 (Operation & Maintenance Agreement) | During Defect Liability Period if any repair and replacement are done, then the warrantee of the equipment shall be extended from the data of such repair and replacement to the period of original equipment warrantee w.r.t. that replaced component. | As per the clause no. 1.3 (page no. 28) Warranty period for SCB/SIB is 2 Years from Date of Supply. As per the clause no. 2.6 (page no. 30) Warranty period for Solar & DC Cables is 1 Year from Date of Supply. As per the clause no. 3.8 (page no. 35) Warranty period for PCU is 5 Years from Date of Supply. As per the clause no. 4.5 (page no. 39) Warranty period for Transformer is 5 Years from Date of Supply. As per the clause no. 5.11 (page no. 49) Warranty period for HT Panel is 2 Years from Date of Supply. As per the clause no. 6.6 (page no. 52) Warranty period for all cables is 1 Year from Date of Supply. As per the clause no. 8.4 (page no. 56) Warranty period for LT Switchgear is 1 Year from Date of Supply. etc. This clause is not inline with the above mentioned clauses. | Technical | Please refer to DLP and Warranty clause of the tender document.
72 | Section V (SCC) | 6/12 | 10 Contractor’s responsibility (GCC clause 32.1.3) | In the matter of connectivity of Plant to DISCOM’s substation, the Owner will take the necessary connectivity permission, however, all the other permissions and clearances as deemed required by the State Agency/DISCOM for Bay allocation, technical/regulatory compliance for interconnection, ROW etc. are to be taken by the Contractor. All the required fees including statutory fees, Supervision charges etc. shall be paid / born by the contractor. | Please confirm that the complete scope of taking all the permissions and clearances as may be required by State Agency / Discom, technical / regulatory compliance for interconnection, ROW etc. shall be in the scope of Customer. Further, ROW of TL shall be in the scope of Owner. | Technical | The terms and conditions of the tender document shall prevail.
73 | Section V (SCC) | 8/12 | 12 Conditions for Issue of Materials (GCC clause 60) | vi) The Owner shall not be liable for delay in supply or non-supply of any materials which the Owner has undertaken to supply where such failure or delay is due to natural calamities, act of enemies, transport and procurement difficulties and any circumstances beyond the control of the Owner. In no case, the Contractor shall be entitled to claim any compensation or loss suffered by him on this account. | Please confirm that Owner shall be fully responsible and liable to supply its scope of items in a timely manner as identified in the L2 schedule. However, in case there is a delay in supply or non-supply of any material which the Owner has undertaken to supply, except Force Majeure conditions, the Contractor shall be entitled to claim any compensation or loss suffered by him on this account. | Contractual | All such situation will be dealt on case to case basis, in line with the provision of the tender document.
74 | Section V (SCC) | 8/12 | 13 Inspection of Works (GCC clause 66) | 66.4 All PV Modules supplied by the Owner at the site shall be inspected at site by the Contractor along with the Owner. In all cases necessary test certificates, guarantee certificate in respect of material/equipment performance shall be furnished by the Contractor. | Please confirm that necessary test certificates, guarantee certificates etc. in respect of material / equipment performance of Owner's supplied material shall be in the scope of the Owner. | Contractual | Necessary test certificates, guarantee certificates etc. in respect to Module supplied by Owner shall be in the scope of Owner. However inspection of Module at site along with generating necessary test certificates, guarantee certificate in respect of Module performance shall be in the scope of Contractor.
75 | Section V (SCC) | 9/12 | 15 Schedule of Rates & Payments (GCC clause 80.1) | Payment of Taxes and Duties | Please confirm the payment of Taxes and Duties as mentioned below a) For Supplies, 100% GST shall be paid on the dispatch of the equipment / material at site. B) For Services, GST will be paid on pro-rata basis against each invoice. | Contractual | The payment will be done on pro rata basis as mentioned under the payment terms based on the individual BBU line item invoices. The respective tax component will be build and paid accordingly.
76 | Section V (SCC) | 9/12 | 15 Schedule of Rates & Payments (GCC clause 80.1) | A. The payment for the Supply Portion of the First Contract (Supply Contract) shall be made as per the following terms and conditions: i) Interest free initial advance (OPTIONAL) of 10% of the Contract Value (i.e., total sum of all the Supply Contract) shall be released to the contractor upon receipt of unconditional acceptance of NOA, detailed Performa invoice of contractor and against submission of unconditional & irrevocable Advance Bank Guarantee (ABG) with a validity period up to date of final commissioning total amounting to 110% of total advance amount. The ABG needs to be submitted in addition to the Contract Performance Security. ii) Seventy percent (70%) payments shall be paid on Pro rata basis against supply, receipt and acceptance of Materials at site on submission of documents (except Advance Bank Guarantee) indicated under clause i) above, Contractor’s detailed invoice & packing list identifying contents of each shipment, evidence of dispatch (GR/ LR copy), Manufacturer’s/ Contractor’s Guarantee certificate of Quality, submission of the certificate by the Executing Agency’s authorized representative that the item(s) have been received and MDCC (Material Dispatch Clearance Certificate) issued by Employer's authorized representative in original. * In case the Interest-free initial advance (OPTIONAL) of 10% of the Contract Value is not availed by the contractor, then this 10% payment amount will be payable along with the point No A ii) along with the 70% payment milestone. * In case the interest free advance is availed by the Contractor and no progress/work is executed at site till the commissioning period or if the contract is terminated due to default of contractor as mentioned under the Contract/tender, thereby not adjusting the advance amount timely, the entire advance amount will be recovered from the Contractor along with one-year SBI MCLR rate. (iii) Ten percent (10%) payments shall be paid against successful erection, testing and commissioning of materials on pro rata basis at site. (iv) Final Ten percent (10%) payment of Supplies shall be paid against submission of the BG of the equivalent amount & against the Operational Acceptance of the plant Facility pursuant to successful Guarantee Tests and demonstration of Performance Ratio (PR) including submission of all as-built drawings and O&M manual. This BG shall be valid for a period of 18 (Eighteen) months from the date of its issuance & will be released after CUF demonstration on completion of first year of O&M, pursuant to the submission of all requisite documentation up to the final acceptance of the Plant facilities. However, in case of any delay, the BG shall be extended suitably. | We request you to kindly provide the following payment terms in Supplies i) 15% Advance against ABG submission of equivalent value ii) 80% on pro-rata basis against supply, receipt of material at site. iii) 5% on commissioning | Contractual | The terms and conditions of the tender document shall prevail.
77 | Section V (SCC) | 9/12 | 15 Schedule of Rates & Payments (GCC clause 80.1) | i) For Freight and Insurance Portion, the payment shall be made in line with Supply Portion of the First Contract, as described in point A (ii) of this clause, without releasing any initial advance. The complete payment of the freight will be done along with the respective deliveries of the supply portion at site. | We request you to kindly provide the following payment terms in Freight and Insurance i) 15% Advance against ABG submission of equivalent value ii) 85% on pro-rata basis against supply, receipt of material at site. | Contractual | The terms and conditions of the tender document shall prevail.
78 | Section V (SCC) | 9/12 | 15 Schedule of Rates & Payments (GCC clause 80.1) | ii) For Erection, Testing and Commissioning Portion, the payment shall be made as detailed below: - (a) Eighty Percent (80%) of the total price of Design, Engineering, Erection, Testing and Commissioning shall be paid on pro-rata basis on completion of installation of equipment on certification by the Engineer-In-Charge/ Project Manager for the quantum of work completed after successful clearance of quality check points involved in the quantum of work billed. (b) Ten Percent (10%) of the total price of Design, Engineering, Erection, Testing and Commissioning shall be paid against successful commissioning of the plant on pro rata basis for the capacity commissioned. (c) Final Ten percent (10%) payment of Services shall be paid against submission of the BG of the equivalent amount & against the Operational Acceptance of the plant Facility pursuant to successful Guarantee Tests and demonstration of Performance Ratio (PR) including submission of all as-built drawings and O&M manual. This BG shall be valid for a period of 18 (Eighteen) months from the date of its issuance & will be released after CUF demonstration on completion of first year of O&M, pursuant to the submission of all requisite documentation up to the final acceptance of the Plant facilities. However, in case of any delay, the BG shall be extended suitably. | We request you to kindly provide the following payment terms in Erection, Testing and Commissioning Portion i) 15% Advance against ABG submission of equivalent value ii) 80% on pro-rata basis against installation completion. iii) 5% on commissioning | Contractual | The terms and conditions of the tender document shall prevail.
79 | Section V (SCC) | 9/12 | 15 Schedule of Rates & Payments (GCC clause 80.1) | iii) For Civil & Allied works portion, of the Second contract, the payment shall be made as detailed below: (a) Eighty Percent (80%) of the total price of Civil Works shall be paid progressively on certification by the Project Manager/ Engineer In - Charge for the quantum of work completed/ Milestones achieved after successful clearance of quality check points involved in the quantum of work. (b) Ten Percent (10%) of the total price of Civil Works shall be paid against successful commissioning of the plant on pro rata basis for the capacity commissioned. (c) Final Ten percent (10%) payment of Civil Works shall be paid against submission of the BG of the equivalent amount & against the Operational Acceptance of the plant Facility pursuant to successful Guarantee Tests and demonstration of Performance Ratio (PR) including submission of all as-built drawings and O&M manual. This BG shall be valid for a period of 18 (Eighteen) months from the date of its issuance & will be released after CUF demonstration on completion of first year of O&M, pursuant to the submission of all requisite documentation up to the final acceptance of the Plant facilities. However, in case of any delay, the BG shall be extended suitably. | We request you to kindly provide the following payment terms in Erection, Testing and Commissioning Portion i) 15% Advance against ABG submission of equivalent value ii) 80% on pro-rata basis against quantum of work completed. iii) 5% on commissioning | Contractual | The terms and conditions of the tender document shall prevail.
80 | Section V (SCC) | 9/12 | 15 Schedule of Rates & Payments (GCC clause 80.1) | Payment Terms | Please confirm that advance shall be released by the Owner within 15 days of ABG submission. | Contractual | Payment will be released as per the terms and conditions laid down under Payment section of the tender document.
81 | Section V (SCC) | 9/12 | 15 Schedule of Rates & Payments (GCC clause 80.1) | Payment Terms | Please confirm that other than advance, rest all payments shall be paid thru LC at Sight. | Contractual | The terms and conditions of the tender document shall prevail.
82 | Section IV (GCC) | 8/79 | 1.1.26 DEFECT LIABILITY PERIOD | DEFECT LIABILITY PERIOD in relation to scope of work means 12 (Twelve) months from the date of Operational acceptance during which the Contractor stands responsible for rectifying all defects/ rejection that may appear in the works executed by the Contractor in pursuance of the Contract and includes warranties against Manufacturing/ Fabrication/ Erection/ Construction defects covering all materials plants, equipment, components and the like supplied by the Contractor, works executed against workmanship defects. | We request you to kindly consider Defect Liability Period for a period of 12 months from the date of commissioning instead of Operational Acceptance. | Contractual | The terms and conditions of the tender document shall prevail.
83 |  | 10/79 | 1.1.48 NTP | NTP means Notice to Proceed subsequent to the placement of LOA/NOA/LOI. NTP will be issued by the owner within a maximum time frame of 90 days from the date of LOA/NOA/LOI, failing which the LOA/NOA/LO shall stand withdrawn without creating any further liability on either party. In such case EMD/PBG, as applicable submitted by the contractor shall be released. | Since Issue of NOA/ LOA/ LOI (as applicable) is considered as the Zero Date (D) and Date of successful commissioning is D + 12 Months hence concept of NTP is not applicable in this Tender. Please confirm. | Contractual | Though NTP is not directly envisaged for this case but there could be exceptional situations wherein NTP release may be required.
84 |  |  | 2.1.b Access by Road | Contractor, if necessary, shall build other temporary access roads to the actual site of construction for his own work at his own cost. The Contractor shall be required to permit the use of the roads so constructed by him for vehicles of any other parties who may be engaged on the project site. The Contractor shall also facilitate the construction of any permanent roads should the construction thereof starts while he is engaged on this work. He shall make allowance in his Tender for any inconvenience he anticipates on such account. Non-availability of access roads, railway siding and railway wagons for the use of the Contractor shall in no case condone any delay in the execution of work nor be the cause for any claim for compensation against the EMPLOYER/ Owner. | Please confirm that all the temporary and permanent access and approach roads shall be in the scope of the Owner. The Contractor shall be provided with hindrance free and encumbrance free sites with all ROW and way leaves with unrestricted access to site. | Contractual | Construction of all temporary and permanent approach road to the site shall be in the scope of Contractor including RoW.
85 |  |  | 6.6 | If at any time the Contractor’s actual progress falls behind the scheduled program, or it becomes apparent that it will so fall behind, the Contractor shall, at the request of the EMPLOYER or the Project Manager/ EIC, prepare and submit to the Project Manager/ EIC a revised program, taking into account the prevailing circumstances, and shall notify the Project Manager/ EIC, of the steps being taken to expedite progress so as to attain Completion of the Facilities within the Time for Completion. If any extension thereof entitled under GCC, or any extended period as may otherwise be agreed upon between the EMPLOYER and the Contractor, Contractor shall submit the revised plan for completion of Facility accordingly. | In case the Contractor's performance is delayed due to any act or omission on the part of the EMPLOYER/ Owner or his authorized representatives, other Contractor's engaged by the Owner, then in addition to the extension of time, the additional cost and expenses shall be provided to the Contractor as well including any expediting cost, if any. | Contractual | All such situation will be dealt on case to case basis, in line with the provision of the tender document.
86 |  |  | 13. Local Conditions 13.1 | The site is being offered to the bidders for Project on “as is where is” basis assuming that bidders have acquainted themselves appropriately with all the local site conditions & no plea will be entertained before/after the award of contract on this. It will be imperative on each bidder to acquaint himself of all local site conditions and factors which may have any effect on the execution of work covered under the Tender Document. | Please confirm that in case of unforeseen conditions, which could not be possibly seen by an experienced Contractor, including removal of any underground hindrances, change in soil conditions, changes in the layout or technological requirements etc. the additional cost and time shall be paid by the Customer to the Contractor. | Contractual | All such situation will be dealt on case to case basis, in line with the provision of the tender document.
87 |  |  | 14. Extension of Time for Commissioning | 14.1 The time for Project commissioning as specified in the SCC is firm & final binding till the final commissioning of the Plant facilities. The Time(s) for Commissioning specified in the SCC shall be extended if the Contractor is delayed or impeded in the Performance of any of its obligations under the Contract due to delay in fulfilment of obligations by the Owner or by the reason of any of occurrence of Force Majeure as provided in the Tender for Force Majeure. 14.2 The Contractor shall at all times use its reasonable efforts to minimize any delay in the Performance of its obligations under the Contract. | Please include the following events as well in extension of time a) Change / variation Order b) Suspension order by Owner due to reasons not attributable to the Contractor, c) Change in Law, d) reasons not attributable to the Contractor e) any other reason as mentioned in the Tender / Contract | Contractual | All such situation will be dealt on case to case basis, in line with the provision of the tender document.
88 |  |  | 17 Contractor to obtain his own Information 17.1 | The Contractor in fixing his cost shall for all purpose whatsoever reason may be, deemed to have himself independently obtained all necessary information for the purpose of preparing his tender and his tender as accepted shall be deemed to have taken into account all contingencies as may arise due to such information or lack of same. The correctness of the details, given in the Tender Document to help the Contractor to make up the tender is not guaranteed. The Contractor shall be deemed to have examined the Contract Documents, to have generally obtained his own information in all matters whatsoever that might affect the carrying out of the works at the scheduled rates and to have satisfied himself to the sufficiency of his offer. | The Bid of the Contractor shall be based on the tender provided by the Owner. The Owner takes the ownership of the defects, errors, inaccuracies, discrepancies, omissions, incorrectness of the any part / requirement of the tender and shall indemnify the Contractor against the same. Please confirm. | Contractual | Owner will exercise his best possible efforts in providing all diligent, available and factual information as it is a case of Own project to SECI. However, if any such situation arises it will be dealt on case to case basis, in line with the provision of the tender document.
89 |  |  | 17 Contractor to obtain his own Information 17.1 | Any error in description of quantity or omission therefrom shall not vitiate the Contract or release the Contractor from executing the work comprised in the Contract according to Drawings and Specifications at the scheduled rates. He is deemed to have known the scope, nature and magnitude of the Works and the requirements of materials and labour involved etc., and as to what all works he has to complete in accordance with the Contract documents whatever be the defects, omissions or errors that may be found in the Documents. | The Bid of the Contractor shall be based on the tender provided by the Owner. The Owner takes the ownership of the defects, errors, inaccuracies, discrepancies, omissions, incorrectness of the any part / requirement of the tender and shall indemnify the Contractor against the same. Please confirm. | Contractual | Owner will exercise his best possible efforts in providing all diligent, available and factual information as it is a case of Own project to SECI. However, if any such situation arises it will be dealt on case to case basis, in line with the provision of the tender document.
90 |  |  | 17 Contractor to obtain his own Information 17.1 | The Contractor shall be deemed to have visited surroundings, to have satisfied himself to the nature of all existing structures, if any, and also as to the nature and the conditions of the Railways, Roads, Bridges and Culverts, means of transport and communication, whether by land, water or air, and as to possible interruptions thereto and the access and egress from the site, to have made enquiries, examined and satisfied himself as to the sites for obtaining sand, stones, bricks and other materials, the sites for disposal of surplus materials, the available accommodation as to whatever required, depots and such other buildings as may be necessary for executing and completing the works, to have made local independent enquiries as to the sub-soil, subsoil water and variations thereof, storms, prevailing winds, climatic conditions and all other similar matters effecting these works. | Please confirm that in case of unforeseen conditions, which could not be possibly seen by an experienced Contractor, including removal of any underground hindrances, change in soil conditions, changes in the layout or technological requirements etc. the additional cost and time shall be paid by the Customer to the Contractor. The Bid of the Contractor shall be based on the tender provided by the Owner. The Owner takes the ownership of the defects, errors, inaccuracies, discrepancies, omissions, incorrectness of the any part / requirement of the tender and shall indemnify the Contractor against the same. Please confirm. | Contractual | All such situation will be dealt on case to case basis, in line with the provision of the tender document.
91 |  |  | 17 Contractor to obtain his own Information 17.1 | He is deemed to have acquainted himself as to his liability of payment of Government Taxes, duties and other charges, levies etc. Any neglect or omission or failure on the part of the Contractor in obtaining necessary and reliable information upon the foregoing or any other matters affecting the Contract shall not relieve him from any risks or liabilities or the entire responsibility from completion of the works at the scheduled rates and times in strict accordance with the Contract. It is, therefore, expected that should the Contractor have any doubt as to the meaning of any portion of the tender Document he shall set forth the particulars thereof in writing to EMPLOYER before bid submission. | Please confirm the following a) Statutory variations in the taxes, duties and levies beyond 7 days prior to the last date of bid submission shall be borne by Owner. B) Introduction of new taxes, duties and levies beyond 7 days prior to the last date of bid submission shall be borne by Owner. | Contractual | The GCC Clause 51 for Change in Law is ample clear in deriving any kind of interpretation regarding the Change in Law event. Same may be referred.
92 |  |  | 17 Contractor to obtain his own Information 17.1 | The EMPLOYER may provide such clarification as may be necessary in writing to Contract, such clarifications as provided by EMPLOYER shall form part of tender Documents. No verbal agreement or inference from conversation with any effect or employee of the EMPLOYER either before, during or after the execution of the Contract Agreement shall in any way affect or modify and of the terms or obligations herein contained. Any change in layout due to site conditions or technological requirement shall be binding on the Contractor and no extra claim on this account shall be entertained. | Please confirm that in case of unforeseen conditions, which could not be possibly seen by an experienced Contractor, including removal of any underground hindrances, change in soil conditions, changes in the layout or technological requirements etc. the additional cost and time shall be paid by the Customer to the Contractor. The Bid of the Contractor shall be based on the tender provided by the Owner. The Owner takes the ownership of the defects, errors, inaccuracies, discrepancies, omissions, incorrectness of the any part / requirement of the tender and shall indemnify the Contractor against the same. Please confirm. | Contractual | Owner will exercise his best possible efforts in providing all diligent, available and factual information as it is a case of Own project to SECI. However, if any such situation arises it will be dealt on case to case basis, in line with the provision of the tender document.
93 |  |  | 19. Force Majeure 19.1 |  | Please confirm that Force Majeure includes the following as well, i.e. quarantine restrictions, epidemic, pandemic etc. | Contractual | Kindly refer S.No. 47 of Amendment-1.
94 |  |  | 19. Force Majeure 19.1 | 19.4 Upon occurrence of such causes, the party alleging that it has been rendered unable as aforesaid, thereby, shall notify the other party in writing by registered notice within 7 (Seven) Days of the alleged beginning thereof giving full particulars and satisfactory evidence in support of its claim. Further, within 14 (Fourteen) days, the Contractor will furnish a detailed Contingency Plan to overcome the effects of the incident and bring the project on its schedule after cessation of the effect of Force Majeure. | It is requested to kindly increase the notice period from 7 days to 14 days and satisfactory evidence to be provided within 30 days of notice instead of 14 days. | Contractual | The terms and conditions of the tender document shall prevail.
95 |  |  | 19. Force Majeure 19.1 | 19.7 If works are suspended by Force Majeure conditions lasting for more than two months, the EMPLOYER/Owner shall have the option of cancelling this Contract in whole or part thereof, at its discretion. | Please confirm that Owner and the Contractor shall have the right to terminate in this referred clause. | Contractual | The terms and conditions of the tender document shall prevail.
96 |  |  | 19. Force Majeure 19.1 | 19.8 The Contractor will not be entitled to claim any compensation for Force Majeure conditions and shall take appropriate steps to insure its men and materials utilized by it under the Contract. | Please confirm that Owner's obligation to Contractor shall remain operational and Owner shall not withheld the payments due citing Force Majeure conditions. | Contractual | All such situation will be dealt on case to case basis, in line with the provision of the tender document.
97 |  |  | 20. Liquidated Damages (LD) 20.1 | Subject to Force Majeure Clause, if the Contractor fails to comply with the Time for Completion /successful commissioning or any extension thereof of Plant facilities in accordance with timelines as mentioned under the SCC, then the Contractor shall pay to the Owner a sum equivalent to half percent (0.5%) per week of the Contract Price for the whole of the facilities as liquidated damages for such default and not as a penalty, without prejudice to the Owner’s other remedies under the Contract subject to the maximum limit of five percent (05%) of Contract Price for the whole of the facilities. | 1. Please confirm that LD levied shall be pro-rata i.e. on part thereof of the undelivered work. 2. LD terms are requested to be modified as 0.05% of the Contract Price per day of delay subject to 5% of the Contract Price. | Contractual | The terms and conditions of the tender document shall prevail.
98 |  |  | 20. Liquidated Damages (LD) 20.1 | 20.2 The Owner shall at its sole discretion upon reaching the maximum LD limit , as an alternative to the Liquidated Damages at its option, get work executed from elsewhere at the risk and cost of the Contractor irrespective of the fact whether the scope of Contract is identical to the original scope of Contract and in case the Owner chooses the alternative course as mentioned, it will be entitled to recover compensation/ damages from the Contractor irrespective of maximum limit prescribed under Clause 20.1. | Please confirm that Limitation of Liability shall supersede this clause. | Contractual | The overall liability for such case will be governed by the overall Limitation of Liability in line with the terms of the tender.
99 |  |  | 20. Liquidated Damages (LD) 20.1 | 20.3 The Owner may by giving (01) one-month notice to the Contractor cancel the Contract without prejudice to the Owner’s right under Clauses 20.1 and 20.2 or any other provisions contained in the Contract to determine the Contract and claim damages from the Contractor. | Kindly elaborate the damages to be claimed under this clause. We understand that Owner shall claim damages only towards delay in achieving the commissioning and in case of risk and cost purchase with the cap of 100% of the Contract Price as Limitation of Liability. | Contractual | The terms and conditions of the tender document shall prevail.
100 |  |  | 25. Termination of contract |  | Please confirm that the Contractor shall also have the right to terminate the Contract due to Owner's default. The payment towards such termination shall be paid by the Owner to the Contractor in similar lines to the payments to be made to the Contractor in case of Termination due to Owner's convenience. | Contractual | Please refer to GCC Clause 25 : Termination of Contract for more details on the same.
101 |  |  | 30. Sub-letting of Works 30.1 | vi) Termination/ Cancellation of Contract Owner is nowhere liable for the communication, acts and deeds and performance of the sub-Contractor as engaged by the principal Contractor. Principal Contractor solely is responsible and liable for the entire execution of project and performance of contract. Subject to poor performance and prolonged delay of the project on account of inefficient sub-letting of the project work, Owner may take a final decision to terminate the contract of the principal Contractor which will be binding and non-revertible and henceforth no plea in this regard shall be entertained. | It is requested to kindly delete the clause "Subject to poor performance and prolonged delay of the project on account of inefficient sub-letting of the project work, Owner may take a final decision to terminate the contract of the principal Contractor which will be binding and non-revertible and henceforth no plea in this regard shall be entertained.". Contractor shall be given the chance to rectify , remedy the default of subcontractor first. | Contractual | The terms and conditions of the tender document shall prevail.
102 |  |  | 32.1 Contractor’s responsibility | 32.1.1 The Contractor shall grade/level the land identified for development of the mentioned Power Plant along with the design, procure, manufacture (including associated purchases and/or subcontracting), install, commission and complete the Facilities, carry out the Guarantee tests with due care and diligence in accordance with the Contract along with interconnecting transmission system including Right of Way for Transmission Line and the comprehensive O&M of the complete facilities for the period as defined under the tender document . It is Contractor’s responsibility to coordinate with state/central agencies in order to get any permission whatsoever, required for successful development & operation of Plant till its desired life. | Right of way is in the Owner's scope. Please confirm. | Contractual | ROW is in the scope of the Contractor.
103 |  |  | 32.1 Contractor’s responsibility | 32.1.2 The Contractor shall acquire, on behalf of Owner, in the Owner’s name, all permits, approvals and/or licenses from all local, state or national government authorities or public service undertakings in the Country/State where the Site is located that are necessary for the setting up of the Plant & operation of Plant till its desired life as mentioned under the Contract, including, but not limited to, entry permits for all imported Owner’s/Employer's Equipment (if any). In this regard, any document required from Owner/ EMPLOYER shall be intimated at least 10 days prior to submission. Contractor has to ensure safe keeping of the documents and diligent use. It is the responsibility of the Contractor to safe keep and return all the original approvals, permits, licenses, certificates and other relevant document generated as a result of the setting up of project and comprehensive O&M process to the Owner. | Please confirm that the referred clause and the complete scope of ROW, statutory clearances, permits, approvals etc. as required in the Project including payments are in the scope of Owner itself. | Contractual | ROW is in the scope of the Contractor.
104 |  |  | 32.1 Contractor’s responsibility | 32.1.4 The Contractor shall acquire in its name all permits, approvals and/or licenses from all local, state or national government authorities or public service undertakings in the country where the Site is located that are necessary for the Performance of the Contract, including, but not limited to, the right of way for the access to site and for erection of transmission lines as applicable, visas for the Contractor’s and Sub-Contractor’s personnel and entry permits for all imported Contractor’s Equipment. The Contractor shall acquire all other permits, approvals and/or licenses that are not the responsibility of the Owner and that are necessary for the Performance of the Contract. | The scope of "the right of way for the access to site and for erection of transmission lines as applicable" shall be in the scope of Owner. Please confirm. | Contractual | The right of way for the access to site and for erection of transmission lines as applicable will be in the scope of the Contractor.
105 |  |  | 33. Other Agencies at Site | 33.1 The Contractor shall have to execute the Work in such place and conditions where other agencies may also be engaged for other works such as site grading, filling, and levelling, electrical and mechanical engineering works, etc. No claim shall be entertained due to Work being executed in the above circumstances. The Contractor shall allow such agencies to use the facilities like roads, etc constructed by the Contractor in order that they are able to carry out their respective scope of works unhindered | In case the Contractor's performance is delayed due to any act or omission on the part of the EMPLOYER/ Owner or his authorized representatives, other Contractor's engaged by the Owner, then in addition to the extension of time, the additional cost and expenses shall be provided to the Contractor as well including any expediting cost, if any. | Contractual | All such situation will be dealt on case to case basis, in line with the provision of the tender document.
106 |  |  | 38. Delays by EMPLOYER/ Owner or his Authorized representatives | 38.1 In case the Contractor's performance is delayed due to any act or omission on the part of the EMPLOYER/ Owner or his authorized representatives, then the Contractor may be given due extension of time for the completion of the Work after proper due diligence by EMPLOYER/ Owner, to the extent such omission on the part of the EMPLOYER/ Owner has caused delay in the Contractor's performance of his Work. 38.2 No adjustment in Contract Price shall be allowed for reasons of such delays and extensions granted except as provided in Tender Document, where the EMPLOYER/ Owner reserves the right to seek indulgence of Contractor to maintain the agreed Time Schedule of Completion. In such an event the Contractor shall be obliged for working by Contractor's personnel for additional time beyond stipulated working hours as also Sundays and Holidays and achieve the completion date/interim targets. | In case the Contractor's performance is delayed due to any act or omission on the part of the EMPLOYER/ Owner or his authorized representatives, other Contractor's engaged by the Owner, then in addition to the extension of time, the additional cost and expenses shall be provided to the Contractor as well including any expediting cost, if any. | Contractual | All such situation will be dealt on case to case basis, in line with the provision of the tender document.
107 |  |  | 43.3 Operational Acceptance | 43.3.6 The start date of the Comprehensive Operation and Maintenance shall be reckoned from the date mentioned in the Operational Acceptance Certificate. | It is requested to kindly take the start date of Comprehensive O&M from the date of commissioning. | Contractual | The terms and conditions of the tender document shall prevail.
108 |  |  | 51. Change in Laws and Regulations | However, any increase in the rate of these taxes, duties and levies beyond the contractual completion period shall be to Contractor's account and any decrease shall be passed on to Owner. | Please confirm that the same is applicable for the contractual completion period with permitted extension of time thereof. | Contractual | If the extension is being provided to the Contractor without any Liquidated Damages based on the reasons not attributable to the default / delay / non-performance/ any other reason related to the Contractor then in such cases treatment shall be done in accordance with the Change in Law clause of GCC.
109 |  |  | 51. Change in Laws and Regulations | However, Change in Law shall not include (i) any change in taxes on corporate income or (ii) any change in any withholding tax on income or dividends distributed to the shareholders of the Contractor, or (iii) any change on account of regulatory measures by the Appropriate Commission. | Any change by Appropriate Commission shall be routed through Change in Law, hence kindly delete "or (iii) any change on account of regulatory measures by the Appropriate Commission." | Contractual | The terms and conditions of the tender document shall prevail.
110 |  |  | 52. General Conditions for Construction and Erection Work | 52.1 Overtime work is permitted in cases of need and the Owner will not compensate the same. Shift working at 2 or 3 shifts per day may become necessary and the Contractor should take this aspect into consideration for formulating his rates. No extra claims will be entertained by the Owner on this account. | Please confirm that the referred clause is applicable only in case of delays due to reasons solely attributable to the Contractor. | Contractual | This clause is applicable in case of default / delay / non-performance/ any other reason attributable to the Contractor. In case of any default arising due to the reasons related to Owner's default, all such cases will be dealt on case to case basis.
111 |  |  | 52. General Conditions for Construction and Erection Work | 52.2 The Contractor must arrange for the placement of workers in such a way that the delayed completion of the Work or any part thereof for any reason whatsoever will not affect their proper employment. The Owner will not entertain any claim for idle time payment whatsoever. | Please confirm that the referred clause is applicable only in case of delays due to reasons solely attributable to the Contractor. | Contractual | This clause is applicable in case of default / delay / non-performance/ any other reason attributable to the Contractor. In case of any default arising due to the reasons related to Owner's default, all such cases will be dealt on case to case basis.
112 |  |  | 53. Design and Engineering | 53.1 The Work covered under this Contract having to be executed by the Contractor on a lump-sum firm price quoted by him, the Owner will not accept any proposals for changes in Value of Contract or extension in time on account of any such changes which may arise to the Contractor's scope of Work as a result of detailed Engineering and thereafter during the execution of Work. | IN case of any change in the already approved design, engineering, drawing / document, executed work by Project Manager, the same shall be routed through Change Order for any additional cost and time implication. Please confirm. | Technical | The terms and conditions of the tender document shall prevail. However please refer to Clause 6 (Civil Works) under Scope of Work section of Technical Specifications for variation suggested in Steel / Foundation works.
113 |  |  | 53. Design and Engineering | 53.3.10 If the Project Manager requests any change in any already approved document and/or in any document based thereon, generally shall be taken care by the Contractor if the change is not causing any major financial impact. | IN case of any change in the already approved drawing / document by Project Manager, the same shall be routed through Change Order for any additional cost and time implication. Please confirm. | Technical | The terms and conditions of the tender document shall prevail. However please refer to Clause 6 (Civil Works) under Scope of Work section of Technical Specifications for variation suggested in Steel / Foundation works.
114 |  |  | 58. Materials to be supplied by Contractor | 58.1 Plant and Equipment The Contractor shall procure and transport all the Plant and Equipment in an expeditious and orderly manner to the Site to achieve completion of activities as per schedule to enable commissioning of the Project by the scheduled commissioning date. Contractor shall deliver supplies at site in accordance to its erection sequence. Owner may hold payment against supplies in case same is delivered more than 03 (Three) months before its erection requirement (except for imported items) | It is requested to kindly delink the supplies with the services (erection). Hence kindly delete "Owner may hold payment against supplies in case same is delivered more than 03 (Three) months before its erection requirement (except for imported items)". | Contractual | The terms and conditions of the tender document shall prevail.
115 |  |  | 67. Tests for Quality of Work | 67.3 If any tests are required to be carried out in conjunction with the Work or materials or workmanship not supplied by the Contractor, such tests shall be carried out by the Contractor and cost of such tests shall be reimbursed by the Owner. | Contractor shall be responsible and liable for its scope of work as defined in the TS. Hence kindly delete this clause. | Contractual | The terms and conditions of the tender document shall prevail.
116 |  |  | 70. Suspension of Works | 70.1 i) Subject to the provisions of sub-para (ii) of this clause, the Contractor shall, if ordered in writing by the Engineer-in-Charge/Project Manager, or his representative, temporarily suspend the Works or any part thereof for such written order, proceed with the Work therein ordered to be suspended until, he shall have received a written order to proceed therewith. The Contractor shall not be entitled to claim compensation for any loss or damage sustained by him by reason of temporary suspension of the Works aforesaid. However, suitable time extension may be considered at the sole discretion of the owner. ii) In case of suspensions of entire Work, ordered in writing by Engineer-in-Charge/Project Manager, for a period of more than 03 (Three) months, the Contractor shall have the option to terminate the Contract. | In terms of the industry practices, in case of suspension due to reasons not attributable to the Contractor or due to Owner's convenience, due to which Contractor is unable to work or the progress of work is impeded, the additional cost and expenses due to such suspension shall be provided by the Owner to the Contractor. The above shall also be applicable in case of Owner's default or non fulfilment of Owner's obligation wherein the Contractor shall be have the right to suspend the work. | Contractual | The terms and conditions of the tender document shall prevail.
117 |  |  | 71. Owner may do Part of Work | 71.1 Upon failure of the Contractor to comply with any instructions given in accordance with the provisions of this Contract the Owner has the alternative right, instead of assuming charge of entire Work, to place additional labour force, tools, equipment and materials on such parts of the Work, as the Owner may designate or also engage another Contractor to carry out the Work. In such cases, the Owner shall deduct from the amount which otherwise might become due to the Contractor, the cost of such work and material with 110% (Hundred & Ten Percent) of the actual cost of works and materials. | We understand the requirement of 110% of the actual cost of works and material to be charged from the Contractor beyond actual cost is inadvertently mentioned and hence may please be removed. Further kindly confirm that Owner shall charge the fair competitive market price only in the referred clause. | Contractual | This clause is as per the ongoing industry practise.
118 |  |  | 72. Possession prior to Completion | 72.1 The Engineer-in-Charge/Project Manager shall have the right to take possession of or use any completed or partially completed Work or part of the Work. Such possession or use shall not be deemed to be an acceptance of any work completed in accordance with the Contract Agreement. If such prior possession or use by the Engineer-in-Charge/Project Manager delays the progress of Work, equitable adjustment in the time of completion will be made and the Contract Agreement shall be deemed to be modified accordingly. | Please confirm that in case the Contractor is ready for commissioning however, the Owner is not ready for commissioning or the commissioning can not be achieved due to reasons not attributable to the Contractor, then in such case, the project shall be considered deemed commissioned from the date of Contractor's readiness of commissioning. The payment terms, defect liability period etc. shall be linked with deemed commissioning thereafter. | Contractual | The terms and conditions of the tender document shall prevail.
119 |  |  | 73. Defects Liability Period | [12 (Twelve) Months Period of Liability from the date of Operational Acceptance] | We request you to kindly confirm that the Defect Liability period shall be 12 months from the commissioning / deemed commissioning of the Project. | Contractual | The terms and conditions of the tender document shall prevail.
120 |  |  | 74.1 Defects Prior to Taking Over | If at any time, before the Work is taken over, the Engineer-in-Charge/Project Manager shall: a) Decide that any works done or materials used by the Contractor or by any Sub-Contractor is defective or not in accordance with the Contract, or that the works or any portion thereof are defective, or do not fulfil the requirements of Contract (all such matters being hereinafter, called `Defects' in this clause), and b) As soon as reasonably practicable, gives to the Contractor notice in writing of the said decision, specifying particulars of the defects alleged to exist or to have occurred, then the Contractor shall at his own expenses and with all speed make good the defects so specified. In case, Contractor shall fail to do so, the Owner may take, at the cost of the Contractor, such steps as may take in all circumstances, be reasonable to make good such defects. The expenditure so incurred by the Owner will be recovered from the amount due to the Contractor. The decision taken by the Owner in this regard towards the amount to be recovered from the Contractor will be final and binding on the Contractor. As soon as the Work has been completed in accordance with the Contract (except in minor respects that do not affect their use for the purpose for which they are intended and have passed the tests on completion, the Owner shall be deemed to have taken over the Work on the date so certified. | Please confirm that the Owner shall rectify the same at fair competitive market price | Contractual | Competitive Market Price / Reasonable Price are all ambiguous terms which doesn’t prevail in market practises. It is the actual risk and cost value which is being delivered by another Contractor / Party on behalf of the defaulted Contractor.
121 |  |  | 80.6 Schedule of Rates to Cover Risks of Delay | The Schedule of Rates shall be deemed to include and cover the risk of all possibilities of delay and interference with the Contractor's conduct of Work which occur from any causes including orders of the EMPLOYER/ Owner in the exercise of his power and on account of extension of time granted due to various reasons and for all other possible or probable causes of delay. | Kindly confirm that the referred clause is only related to the extension of time provided by the Owner due to reasons solely attributable to the Contractor. | Contractual | No
122 |  |  | 84. Notice of Claims for Additional Payments | 84.1 Should the Contractor consider that he is entitled to any extra payment for any extra/ additional Works or Material change in original Specifications carried out by him in respect of Work he shall forthwith give notice in writing to the Engineer-in-Charge/Project Manager that he claims extra payment. Such notice shall be given to the Engineer-in-Charge/Project Manager upon which Contractor bases such claims and such notice shall contain full particulars of the nature of such claim with full details of amount claimed. Irrespective of any provision in the Contract to the contrary, the Contractor must intimate his intention to lodge claim on the Owner within 10 (Ten) days of the commencement of happening of the event and quantify the claim within 30 (Thirty) days, failing which the Contractor will lose his right to claim any compensation /reimbursement/ damages etc. or refer the matter to arbitration. Separate bills shall be raised for the extra claim. | It is requested to kindly include the additional costs, expenses etc. in account of idling charges, incidental costs, other expenses etc. which the Contractor has incurred / will be incurred in addition to extra/ additional Works or Material change in original Specifications | Contractual | The terms and conditions of the tender document shall prevail.
123 |  |  | 84. Notice of Claims for Additional Payments | 84.2 Engineer-in-Charge/Project Manager shall review such claims within a reasonably period of time and cause to discharge these in a manner considered appropriate after due deliberations thereon. However, Contractor shall be obliged to carry on with the Work during the period in which his claims are under consideration by the Owner, irrespective of the outcome of such claims, where additional payments for Works considered extra are justifiable in accordance with the Contract provisions, Owner shall arrange to release the same in the same manner as for normal Work payments. Such of the extra works so admitted by Owner shall be governed by all the terms, conditions, stipulations and specifications as are applicable for the Contract. Settlement of all extra claims shall be taken up after Project commissioning. | Since the release of claims shall be in accordance with the normal work payments or when the claims fall due, hence kindly delete the following "Settlement of all extra claims shall be taken up after Project commissioning.". | Contractual | The terms and conditions of the tender document shall prevail.
124 |  |  | 85 Payment of Contractor's Bill | 85.1 Payment due to the Contractor shall be made by the Owner either by e-Banking or by Account Payee Cheque forwarding the same to registered office or the notified office of the Contractor. In no case, will Owner be responsible if the cheque is mislaid or misappropriated by unauthorized person/ persons. In all cases, the Contractor shall present his bill duly pre-receipted on proper revenue stamp & payment shall be made in Indian Currency only. 85.2 In general payment of final bill shall be made to Contractor within 60 days of the submission of bill on joint measurements, after completion of all the obligations under the Contract against the final completion. | It is requested to kindly make the following payment mode a) All the payments except Advance shall be paid through LC at Sight. B) Advance shall be paid within 15 days from the submission of ABG of equivalent amount. In case of delay in the payments to the Contractor, the interest @ SBI's MCLR rate shall be paid on the delayed payment for the delayed period. | Contractual | The terms and conditions of the tender document shall prevail.
125 |  |  | 90. Deductions from the Contract Price | 90.1 All costs, damages or expenses which Owner may have paid or incurred, which under the provisions of the Contract, the Contractor is liable/ will be liable, will be claimed by the Owner. All such claims shall be billed by the Owner to the Contractor regularly as and when they fall due. Such claims shall be paid by the Contractor within 15 (Fifteen) days of the receipt of the corresponding bills and if not paid by the Contractor within the said period, the Owner may, then, deduct the amount from any moneys due including Contract Performance Security or becoming due to the Contractor under the Contract or may be recovered by actions of law or otherwise, if the Contractor fails to satisfy the Owner of such claims. | Please confirm that in similar lines, All costs, damages or expenses which Contractor may have paid or incurred, which under the provisions of the Contract, or due to the reasons not attributable to the Contractor, the Owner is liable/ will be liable, will be claimed by the Contractor. All such claims shall be billed by the Contractor to the Owner regularly as and when they fall due. Such claims shall be paid by the Owner to the Contractor within 15 (Fifteen) days of the receipt of the corresponding bills. | Contractual | The terms and conditions of the tender document shall prevail.
126 | Project Particulars | Pg. 5-329 | Module Mounting Structure Type | East-West Fixed Tilt (Tilt angle: 5°, Azimuth angle: - 90°/+90°) Minimum inter-row spacing shall be 1 m. | Pleases confirm project type. 1 Tracker based ?? 2 Fixed types ? | Technical | Fixed tilt.
127 | Project Particulars | Pg. 5-329 | Site Location and Land Details | Available Land Area ,1020 acres (approx.) | Please share drawing Cad format or KMZ format ,Please confirm boundary scope also. | Technical | The geo-referenced CAD file of tentative land layout attached in Annexure-C to Section-VII. Construction of chain link fence around entire plant area is in scope of the Contractor.
128 | Project Particulars |  | Distance to interconnecting substation | 18 km (approx.) | Please confirm the ROW work . | Technical | ROW is in scope of the Contractor.
129 | 2 FUNCTIONAL GUARANTEE TESTS FOR SOLAR PV PLANT | ANNEXURE-A Page 3 of 10 | .1 PERFORMANCE RATIO GUARANTEE TEST | A Performance Ratio Guarantee test shall be commenced within 60 days of the commissioning of Plant Facilities to demonstrate that the plant has achieved the Guaranteed Performance Ratio in line with requirements under section VII of the bidding document. This will be one of the pre-conditions for the Plant Operational Acceptance | Please confirm the minimum/guaranteed performance ratio to be quoted. | Technical | Kindly refer Clause 1 of Scope of Works. Performance Ratio at 220 kV side of Plant Pooling Substation - 85.90%
130 | 3 FUNCTIONAL GUARANTEE TESTS FOR SOLAR PV PLANT | ANNEXURE-A Page 10 of 10 | 3 LIQUIDATED DAMAGES FOR SHORTFALL IN PR | For every 0.01 shortfall in PR below the specified PR value, liquidated damages of 1% of the Contract Value shall be levied. In case the Plant PR Shortfall is more than 0.05 below the specified PR value | Already there are LD on shirt fall in generation/CUF. Bidder request to void LD on PR . | Technical | The terms and conditions of the tender document shall prevail.
131 | ANNEXURE 2 Functional Guarantees | 38 | 1. Annual CUF Guarantee | Reference Irradiation for the site = 2008 kWh/m2 | Please provide monthly GHI profile. | Technical | Solargis TMY (01/01/1999 to 31/12/2021) file has been used for energy yield estimation. The bidder may use the same for bidding. However, it shall be noted that radiation correction will be done based on annual radiation only.
132 | ANNEXURE 2 Functional Guarantees | 38 | 1. Annual CUF Guarantee | Reference Irradiation for the site = 2008 kWh/m2 | Please confirm the minimum/guaranteed CUF to be quoted. | Technical | Kindly refer Clause 1 of Scope of Works. Capacity Utilization Factor at 220 kV side of Interconnecting Substation - 21.66%
133 | A Electrical System | Pg. 28-329 | 1 String Combiner Box / String Isolator Box | 1.2.3 Every SCB input shall be provided with fuses on both positive and negative side. In case of negative grounded system, fuse at positive side only is acceptable. The rating of the fuses shall be selected such that it protects the modules from reverse current overload. The fuses shall be ‘gPV’ type conforming to IEC 60269-6. | KEC prepose SCB fuses only for Positive side Pls confirm | Technical | In case of negative grounded system, fuse at positive side only is acceptable.
134 | Solar and DC Cables | Pg. 29-329 | Cables shall be sized based on the following considerations | (ii) In case of central inverters, average voltage drop in the cables (from PV Modules to PCU) shall be limited to 1.5 % of the rated voltage. In case of string Inverters, average voltage drop (from PV module to string inverter) shall be limited to 0.5% of the rated voltage drop. The Contractor shall provide voltage drop calculations in excel sheet. | Please share DC Size Cable parameter . 1- DC Cable 6 Sq. – cable Conductor temperature (70 deg 90 deg,) 2- AC Side – Please share completed AC side losses also. | Technical | Solar and DC cable size shall be decided as per Clause 2.5 of Technical Specifications. AC cable losses are specified in Clause 6.5 of Technical Specifications.
135 | Solar and DC Cables | Pg. 30-329 | Cables shall be sized based on the following considerations | Solar cables may be laid over ground on GI cable trays / underground through Double Wall Corrugated (DWC) HDPE conduits from PV String (Series connection of PV Modules) to SCB/String Inverter. The size of the conduit or pipe shall be selected on the basis of 40% fill criteria. Solar cable terminations shall be made with connectors complying IS 16781 / IEC 62852. The connectors shall have degree of protection of IP 68. | KEC – Proposes Solar cables laying only for HDPE pipe kindly confirm. | Technical | Query not clear.
136 | Earthing of PV array field | Pg. 63-329 | Earthing of PV array field | All PV Modules, Module Mounting Structures (MMS) and String Combiner Box (SCB) structures in the PV array field shall be bonded to the earthing system by two distinct connections. | Module earthing- serrated or module to module earthing, please confirm. | Technical | PV Module is frameless. So, module to module earthing is not required. Back rail of module shall be earthed as per manufacturer recommendation.
137 | SCADA | Pg. 72-329 | 14.9 Software Licences | The Contractor shall provide software license for all software being used in Contractor’s System. The software licenses shall be provided for the project and shall not be hardware/ machine-specific | Pls confirm number of software licence is required. | Technical | Type and number of software licences shall be as per design requirement. However, minimum ten web clients shall be provided as per Clause 14.5.7 of Technical Specifications. The terms and conditions of the tender document shall prevail.
138 | Power Transformer | Pg. 74-329 | Power Transformer | Three nos. of 100 MVA, 33/220 kV Power Transformer shall be provided in line with “Standard Technical Specifications of Transformer(s) for Solar Park pooling station” issued by Central Electricity Authority (CEA). | Pls Share Complete technical spec. of power transformer | Technical | Detailed Technical Specifications of Power Transformer are mentioned in “Standard Technical Specifications of Transformer(s) for Solar Park pooling station” issued by Central Electricity Authority (CEA).
139 | General Technical Parameters | Pg. 84-329 | General Technical Parameters | Rated short-time withstand current 40 kA or 50 kA for 1 s (as applicable) | KEC request to you Please confirm KA rating 220 kV | Technical | Kindly refer S.No.24 of Amendment-1.
140 | Technical Parameters | Pg. 88-329 | Disconnector-Technical Parameters | Rated peak withstand current for isolator & earth switch 100 kAp or 125 kAp (as applicable) | Pls confirm. Rated peak withstand current for isolator & earth switch. | Technical | Kindly refer S.No.25 of Amendment-1.
141 | Technical Parameters | Pg. 108-329 | CCTV Camera | CCTV Cameras along with monitoring stations (sufficient numbers) and all other accessories required for its proper operation must be installed to have complete coverage of following areas for 24 hours. (i) Main entry: Covering all the entry/exit (ii) Along the Plant Perimeter: Covering complete perimeter of Plant Area to capture all possible intrusion | Covering complete perimeter of PV Plant Area & Substation. | Technical | Plant area includes PV Plant area and Substation. The terms and conditions of the tender document shall prevail.
142 | Area Grading and Land Development | Pg. 117-329 | Area Grading and Land Development | It shall be ensured that the land grading and levelling is done properly to ensure for free flow of surface run-off and the grade levels shall be fixed with respect to high flood level at site, drainage pattern and system requirements. It shall be ensured that the land is used optimally to have maximum solar power generation considering full utilization of the plot areas. It is advisable to follow the natural flow of water at the ground as far as possible for drainage design | We are flowing natural counter file for MMS installation Please confirm. | Technical | Kindly refer Clause 6.6.1 of Scope of Works. For MMS installation, local grading and levelling shall be done at locations where the ground slope is greater than either 6° along N-S or 5° along E-W direction. MMS installation may follow natural terrain where the ground slope is lesser than either 6° along N-S or 5° along E-W direction. The terms and conditions of the tender document shall prevail.
143 | Dry Cleaning System | Pg. 150-329 | Dry Cleaning System | Supplier Qualification: The Robotic Cleaning System Supplier/Sub-Contractor must have experience of having successfully completed Design, Engineering, Installation, Testing and Commissioning of Robotic Module Cleaning systems for at least 2 Solar PV Projects of minimum capacity of 5 MW in the last 5 years. Such systems must have been in satisfactory operation for at least 12 months from the date of Commissioning. The Contractor shall submit supporting documents as credentials, including Purchase Orders, Commissioning Reports, Performance Certificate of | Please confirm cleaning cycle for months. | Technical | Only wet type cleaning system is allowed. Kindly refer Clause 6.19 of Scope of Works.
144 | Annexure – J | Pg. 326-329 | PV Module PAN File | PVObject_=pvModule | Kec request you please share Module pan file OND format.& Module Dimension. | Technical | PV Module PAN file is attached in Annexure-J to Section-VII. Module dimensions are also available in the PAN file. OND file is applicable to inverter, not PV Module. Since inverter is in the scope of the Contractor, OND file shall be chosen by the bidder.
145 | Annexure – D |  | Tender Drawings |  | Please share indicative single Line Diagram with SS & PSS end both. & Pls Confirm scope of work PSS end | Technical | The design parameters of 220 kV Plant Pooling Substation (Quantity of 33/220 kV Transformers, Switching Scheme, No. of circuits in 220 kV transmission line) required for development of SLD are provided in Clause 1 of Scope of Works. Indicative SLD of Interconnecting Substation is attached in Annexure-K to Section-VII. Scope of works at Interconnecting Substation are mentioned in Section-VII(A).
146 | Annexure – D |  | Tender Drawings | SCADA | Please share indicative Drawing SCADA System. | Technical | SCADA drawing shall be developed based on the specifications provided in Clause 14 of Technical Specifications.
147 | Annexure – D |  | Tender Drawings | 33/ 220 kV Substations. | Please share complete technical specification – 33/ 220 kv Substations - With detail CT- PT - Battery Bank - | Technical | Technical Specifications of Plant Pooling Substation Equipment are provided Clause 19 of Section-VII(B).
148 | Qualification-1.2 | 67 of 219 | 1.2 | The bidder should have experience in EPC execution of Ground mounted Solar PV Projects on Turnkey basis including Design, Supply (Supply of Modules/Inverters can be inclusive or exclusive in the bidder’s scope in the past experience), Installation and Commissioning of Grid connected Solar PV Power Plant of cumulative Capacity not less than 120 (One Hundred and Twenty) MW in last seven Financial years as on last date of bid submission. However, such Grid connected Solar PV Power Plant capacity must have been in satisfactory operation for at least six (06) months prior to the last date of bid submission. | Request for modification as below The bidder should have experience in EPC execution of Ground mounted Solar PV Projects on Turnkey basis including Design, Supply (Supply of Modules/Inverters can be inclusive or exclusive in the bidder’s scope in the past experience), Installation and Commissioning of Grid connected Solar PV Power Plant of cumulative Capacity not less than 100MW (One Hundred) MW in last seven Financial years as on last date of bid submission. However, such Grid connected Solar PV Power Plant capacity must have been in satisfactory operation for at least six (06) months prior to the last date of bid submission. | Contractual | The terms and conditions of the tender document shall prevail.
149 | ITB-15.1 | 63 of 219 | ITB-15.1 | The bid validity period shall be 180 (One Hundred and Eighty Days) from the date of opening of Techno-Commercial Bid | Request for modification as below concerning the market volatility: bid validity period shall be 120 (One Hundred and Twenty Days) from the date of opening of Techno-Commercial Bid | Contractual | The terms and conditions of the tender document shall prevail.
150 | GCC-3 | 153 of 219 | GCC -3 | The Time for Commissioning for the cumulative capacity of 300 MW Ground mounted Solar PV Power Plant at Ramagiri along with other associated equipment as per this tender document in total shall be 12 (Twelve) Months from the Date of the Notification of Award NOA/LOA/LOI. | Request to modify as below: The Time for Commissioning for the cumulative capacity of 300 MW Ground mounted Solar PV Power Plant at Ramagiri along with other associated equipment as per this tender document in total shall be 18 (Eighteen) Months from the Date of the Notification of Award NOA/LOA/LOI. | Contractual | Kindly refer S.No. 49 and S.No. 50 of Amendment-1.
151 |  |  |  |  | We intend to participate in the TENDER on the basis the technical and financial capabilities of our AFFILIATE company. Whereas , the Tender document’s eligibility clause does not allow the usage of Bidder’s AFFILIATE company credentials for meeting the Eligibility Criteria of the Tender as per clause 1.3.7. | Contractual | Kindly refer S.No. 46 of Amendment-1.
152 |  |  |  |  | We would like to participate the bid in the name of AFFILIATE company and in order to qualify and meet the technical qualification requirement of tender, we kindly request to allow the AFFILIATE work experience credentials as a supporting document meeting the technical QR conditions as stipulated in Route I ( I (a) &I (b)) mentioned above of the NIT. We also request to consider that to meet the financial eligibility conditions bidder can meet the requirement of MAAT/ Net worth/Working capital based on the strength of its Subsidiary (ies) and/or Holding company or Subsidiaries of its Holding companies wherever applicable in case the Bidder does not satisfy or meet the criteria on its own/standalone entity basis. | Contractual | Kindly refer S.No. 46 of Amendment-1.
153 | Project Particulars and ANNEXURE 2 Functional Guarantees | Page No.6 of 329 and 318 of 329 |  |  | As per RFP requirement, we (Bidder) need to provide 85.90% PR at plant end 220kV Line Bay and AC CUF 21.66% (569.225MU) at 220kV bay at Interconnecting CTU substation. However as per SolarGIS data, relevant losses we (the Bidder) are able to achieve below figures. 1. PR at 220kV Line bay at Pooling substation : 81% 2. Generation/CUF at 220kV bay at CTU substation : 556MU (21.15%) The corresponding SolarGIS data and PVsyst reports attached. We (Bidder) are requesting the employer to please clarify that is the PR and CUF values will be going to amended? (means are you(employer) going to reducing the values) or can we participate with our achieved values? As it is difficult to achieve the mentioned values. | Technical | 1. Kindly refer the formula of Performance Ratio mentioned in Clause 2.1.1 of Annexure-A (PG Test Procedure) to Section-VII. Performance Ratio is corrected to 25°C. PR value given by PVsyst is not corrected to 25°C. 2. Kindly refer S.No.5 of Amendment-1.

## Amendment-1
Tender No. SECI/C&P/OP/11/0006/2022-23 Dated: 13/04/2023
DESIGN, ENGINEERING, SUPPLY (EXCEPT PV MODULES), CONSTRUCTION, ERECTION, TESTING & COMMISSIONING OF 300 MW (AC) GROUND MOUNTED Ramagiri, Andhra Pradesh
S. No. | Section | Page No. | Clause | Original Version | Amendment
1 | Section-VII(A) - Scope of Works | 3 of 20 | 1 | Module Mounting Structure Type: East-West Fixed Tilt (Tilt angle: 5°, Azimuth angle: - 90°/+90°) Minimum inter-row spacing shall be 1 m. | Module Mounting Structure Type: East-West Fixed Tilt (Tilt angle: 5°-15°, Azimuth angle: - 90°/+90°) Minimum inter-row spacing shall be 1 m.
2 | Section-VII(A) - Scope of Works | 3 of 20 | 1 | Available Land Area: 1020 acres (approx.) | Available Land Area: 921.5 acres (approx.)
3 | Section-VII(A) - Scope of Works | 4 of 20 | 1 | Transmission Line from Pooling Substation to Interconnecting Substation: 220 kV Single Circuit | Transmission Line from Pooling Substation to Interconnecting Substation: 220 kV Single Circuit on Double Circuit Tower
4 | Section-VII(A) - Scope of Works | 4 of 20 | 1 | Hourly rainfall intensity for storm water drainage: 75 cm/hr | Hourly rainfall intensity for storm water drainage: 75 mm/hr
5 | Section-VII(A) - Scope of Works | 4 of 20 | 1 | Performance Ratio at 220 kV side of Plant Pooling Substation: 85.90% | Performance Ratio at 220 kV side of Plant Pooling Substation: 85.30% PR shall be adjusted for any shortfall due to module performance that is not attributable to the Contractor.
6 | Section-VII(A) - Scope of Works | 4 of 20 | 1 | Capacity Utilization Factor at 220 kV side of Interconnecting Substation: 21.66% | Capacity Utilization Factor at 220 kV side of Interconnecting Substation: 21.51% CUF shall be adjusted for any shortfall due to module performance that is not attributable to the Contractor.
7 | Section-VII(A) - Scope of Works | 6 of 20 | 3.3 | … Design calculations and sheets (licenced software as well as design templates) … | … Design calculations and sheets …
8 | Section-VII(A) - Scope of Works | 7 of 20 | 4.1 | Supply of Solar PV Modules is not in the scope of the EPC Contractor. PV Modules will be supplied by SECI from 1st September, 2023 to 31st May, 2024. … | Supply of Solar PV Modules is not in the scope of the EPC Contractor. PV Modules will be supplied by SECI from D+3 to D+11 (D = Zero Date). …
9 | Section-VII(A) - Scope of Works | 7 of 20 | 4.4 | Solar Cables of appropriate size and rating from PV Modules to SCB / IPC / String Inverter along with straight/Y-connectors, ferrules, conduits, cable ties and other materials required for cable laying and termination at both the ends. | Solar Cables of appropriate size and rating from PV Modules to SCB / IPC / String Inverter along with straight/Y-connectors/branch connectors, ferrules, conduits, cable ties and other materials required for cable laying and termination at both the ends.
10 | Section-VII(A) - Scope of Works | 8 of 20 | 4.14 | 33/220 kV Pooling Substation with required number of 33 kV Switchgear Panels (including three spares – one spare per each bus section), three nos. of 100 MVA, 33/220 kV transformers, five nos. of 220 kV Bays (Three Transformer Bays, One Line Bay & One Bus Coupler Bay) including Substation Automation System. | 33/220 kV Pooling Substation with required number of 33 kV Switchgear Panels (including three spares – one spare per each bus section), three nos. of 100 MVA, 33/220 kV transformers, five nos. of 220 kV Bays (Three Transformer Bays, One Line Bay & One Bus Coupler Bay) including Substation Automation System. Busbars, Equipment of Line Bay and Bus Coupler Bay shall be suitable for evacuation of 380 MW.
11 | Section-VII(A) - Scope of Works | 8 of 20 | 4.15 | 220 kV Over Head Transmission Line / Under Ground Cable including Towers, Conductors, Insulators, Cable Termination Kits and associated accessories from 33/220 kV Pooling Substation to Interconnecting Substation as per CTU drawings/specifications including Right of Way, permits and approvals, CTU supervision and maintenance charges. | 220 kV Over Head Transmission Line / Under Ground Cable (suitable for evacuation of 380 MW) including Towers, Conductors, Insulators, Cable Termination Kits and associated accessories from 33/220 kV Pooling Substation to Interconnecting Substation as per CTU drawings/specifications including Right of Way, permits and approvals, CTU supervision and maintenance charges. The bidder shall comply with the directions of CTU regarding sharing of multi-circuit towers with other renewable energy developers near the interconnecting substation. Charges payable for sharing of multi-circuit towers shall be borne by the Contractor.
12 | Section-VII(A) - Scope of Works | 8 of 20 | 4.16 | 220 kV bay at interconnecting substation as per CTU drawings/specifications including shifting or replacement of substation equipment / materials, permits and approvals, CTU supervision and maintenance charges. | 220 kV bay at interconnecting substation (suitable for evacuation of 380 MW) as per CTU drawings/specifications including shifting or replacement of substation equipment / materials, permits and approvals, CTU supervision and maintenance charges.
13 | Section-VII(A) - Scope of Works | 11 of 20 | 5.16 | Installation, Testing and Commissioning of 220 kV Over Head Transmission Line / Underground Cable from 33/220 kV Pooling Substation to Interconnecting Substation as per CTU drawings/specifications including Right of Way, permits and approvals, CTU supervision and maintenance charges. | Installation, Testing and Commissioning of 220 kV Over Head Transmission Line / Underground Cable from 33/220 kV Pooling Substation to Interconnecting Substation as per CTU drawings/specifications including Right of Way, permits and approvals, CTU supervision and maintenance charges. Shutdown of other circuits of shared multi-circuit towers for stringing and/or hot line stringing at the shared multi-circuit towers shall be the responsibility of the Contractor.
14 | Section-VII(A) - Scope of Works | 12 of 20 | 6.1 | ... Contour map attached in Annexure – D is only for reference and general information of the bidder. … | ... Contour map attached in Annexure – C is only for reference and general information of the bidder. …
15 | Section-VII(A) - Scope of Works | 13 of 20 | 6.6.1 | … Any variation in weight of steel excluding accessories and fasteners (calculated based on GFC drawing issued by SECI) up to ± 10% of 28.5 tons/MWp on account of reasons, not limited to change in module rating, dimensions & weight, shall be deemed to be included in the quoted price. No compensation/deduction for cost of material, fabrication, transport, assembly and erection of MMS at site for any variation in weight of steel (excluding accessories and fasteners) up to ± 10% of 28.5 tons/MWp shall be done by SECI. | … Any variation in weight of steel excluding accessories and fasteners (calculated based on GFC drawing issued by SECI) up to ± 5% of 28.5 tons/MWp on account of reasons, not limited to change in module rating, dimensions & weight, shall be deemed to be included in the quoted price. No compensation/deduction for cost of material, fabrication, transport, assembly and erection of MMS at site for any variation in weight of steel (excluding accessories and fasteners) up to ± 5% of 28.5 tons/MWp shall be done by SECI.
16 | Section-VII(B) - Technical Specifications | 8 of 143 | 2.8.4 | Solar cables may be laid over ground on GI cable trays / underground through Double Wall Corrugated (DWC) HDPE conduits from PV String (Series connection of PV Modules) to SCB/String Inverter. The size of the conduit or pipe shall be selected on the basis of 40% fill criteria. Solar cable terminations shall be made with connectors complying IS 16781 / IEC 62852. The connectors shall have degree of protection of IP 68. | Solar cables or group of solar cables combined through branch connector may be laid over ground on GI cable trays / underground through Double Wall Corrugated (DWC) HDPE conduits from PV String (Series connection of PV Modules) to SCB/String Inverter. The size of the conduit or pipe shall be selected on the basis of 40% fill criteria. Solar cable terminations shall be made with connectors complying IS 16781 / IEC 62852. The connectors shall have degree of protection of IP 68.
17 | Section-VII(B) - Technical Specifications | 18 of 143 | 4.6.1.1(iii) | New clause | Tank vacuum test & pressure test as per CBIP manual
18 | Section-VII(B) - Technical Specifications | 18 of 143 | 4.6.1.3 | Type and Special tests are not required for auxiliary transformers of rating including 100 kVA and below. However, auxiliary transformer energy efficiency shall correspond to 3-star BEE rating or better as per BIS guidelines. The Contractor shall demonstrate the same during routine tests. | Type tests mentioned in Clause 4.6.1.1(ii) & (iii) shall be performed for auxiliary transformers. Special tests are not required.
19 | Section-VII(B) - Technical Specifications | 29 of 143 | 5.12.1 | … Functional requirements - Relevant parts of IEC 60255-100 series … | … VOID …
20 | Section-VII(B) - Technical Specifications | 40 of 143 | 11.2.2 | The earth electrode shall be made of high tensile low carbon steel rod, molecularly bonded by high conductivity copper on outer surface with coating thickness not less than 250 micron as per relevant standards. Suitable earth enhancing material shall be filled around the electrode to lower the resistance to earth. Inspection chamber and lid shall be provided as per IS 3043. | The earth electrode shall be made of high tensile low carbon steel rod, molecularly bonded by high conductivity copper on outer surface with coating thickness not less than 250 micron as per relevant standards. Suitable earth enhancing material shall be filled around the electrode to lower the resistance to earth. Inspection chamber and lid shall be provided as per IS 3043. For Plant Pooling Substation earthing, mild steel rod may be used as earth electrode.
21 | Section-VII(B) - Technical Specifications | 43 of 143 | 12.1 | Lightning Protection System (LPS) for the entire plant except plant pooling substation against direct lighting strokes shall be provided as per IS/IEC 62305:2010. | Lightning Protection System (LPS) for the entire plant except buildings and plant pooling substation against direct lighting strokes shall be provided as per IS/IEC 62305:2010 or NF C 17-102. Lightning Protection System for buildings shall be provided as per IS/IEC 62305:2010.
22 | Section-VII(B) - Technical Specifications | 43 of 143 | 12.3 | Air terminals, down conductors and earth termination system shall be designed as per relevant parts of IS/IEC 62305:2010. | Air terminals, down conductors and earth termination system shall be designed as per relevant parts of IS/IEC 62305:2010 or NF C 17-102.
23 | Section-VII(B) - Technical Specifications | 43 of 143 | 12.5 | Type test reports as per IS/IEC 62305:2010 shall be submitted during detailed engineering for approval. | Type test reports as per IS/IEC 62305:2010 or NF C 17-102 shall be submitted during detailed engineering for approval.
24 | Section-VII(B) - Technical Specifications | 63 of 143 | 19.2 | … Rated short-time withstand current: 40 kA or 50 kA for 1s (as applicable) Rated peak withstand current: 100 kAp or 125 kAp (as applicable) … | … Rated short-time withstand current: 40 kA for 1s Rated peak withstand current: 100 kAp …
25 | Section-VII(B) - Technical Specifications | 66 of 143 | 19.5.1 | … Rated short-time withstand current for isolator & earth switch: 40 kA or 50 kA for 1s (as applicable) Rated peak withstand current for isolator & earth switch: 100 kAp or 125 kAp (as applicable) … | … Rated short-time withstand current for isolator & earth switch: 40 kA for 1s Rated peak withstand current for isolator & earth switch: 100 kAp …
26 | Section-VII(B) - Technical Specifications | 71 of 143 | 19.6.1 | … Current for pressure relief test: 40 kA or 50 kA (as applicable) … | … Current for pressure relief test: 40 kA …
27 | Section-VII(B) - Technical Specifications | 73 of 143 | 19.7.1 | … Rated short time thermal withstand current: 40 kA / 50 kA for 1s (as applicable) Rated dynamic current: 100 kAp / 125 kAp (as applicable) … | … Rated short time thermal withstand current: 40 kA for 1s Rated dynamic current: 100 kAp …
28 | Section-VII(B) - Technical Specifications | 88 of 143 | 1.4.2 | Design of steel structures shall conform to IS: 800, 801 or 802 as applicable. Design of concrete structures shall conform to IS: 456 and IS: 13920. For design of liquid retaining structure IS: 3370 shall be followed. Only in case of non-availability of Indian standard, equivalent American or British standard may be used for design with prior approval of the Engineer and the contractor shall submit proper justification for the same along with his request to the Engineer for review and approval, and the decision of the Engineer shall be final and binding. | Design of steel structures shall conform to IS: 800, 801 or 802 as applicable. Ductile design and detailing as per IS 13920 shall be followed in concrete structures except in case of concrete support structure upto plinth level supporting open installations of inverter transformers, control panels at ICR/LCR etc. wherein the detailing shall conform to IS 456 and SP 34. For design of liquid retaining structure IS: 3370 shall be followed. Only in case of non-availability of Indian standard, equivalent American or British standard may be used for design with prior approval of the Engineer and the contractor shall submit proper justification for the same along with his request to the Engineer for review and approval, and the decision of the Engineer shall be final and binding.
29 | Section-VII(B) - Technical Specifications | 94 of 143 | 3.9.7 | … For reference, the standard pile test procedures for compression & pull out and lateral load test given Annexure – 3A and 3B of this section. … | … For reference, the standard pile test procedures for compression & pull out and lateral load test given Annexure – G of this section. …
30 | Section-VII(B) - Technical Specifications | 115 of 143 | 16.2.1 | MCR Office building shall be provided as per drawing titled ‘MCR Building: Plan, Elevation, Sections and Finishing Details’ furnished under Annexure-C. Separate building (MCR Equipment building) shall be provided for housing the electrical equipment. | MCR Office building shall be provided as per drawing titled ‘MCR Building: Plan, Elevation, Sections and Finishing Details’ furnished under Annexure-D. Separate building (MCR Equipment building) shall be provided for housing the electrical equipment.
31 | Section-VII(B) - Technical Specifications | 138 of 143 | 38.1.3 | 200 long 20 dia. rods shall be welded to the pole at 300 mm C/c for access to the device for maintenance purpose. | VOID
32 | Section-VII(B) - Technical Specifications | 138 of 143 | 38.2.1 | SCB/String Inverter shall be mounted on a structural steel supporting frame comprising of ISMC 75 columns at both ends, horizontal framing members and members for cable support. | SCB/String Inverter shall be mounted on a structural steel supporting frame comprising of ISMC columns at both ends, horizontal framing members and members for cable support. Minimum size for column members shall be ISMC 75.
33 | Section-VII(B) - Technical Specifications | 138 of 143 | 38.3 | New clause | 38.3 LA Mast and Foundation (Other than Sub-station) 38.3.1 LA Mast shall be self-supporting structure with GI tubular pole of required height. The pole shall conform to IS 2713. 38.3.2 The pole shall be supported on RCC pedestal and foundation structure through base plate and anchor bolt assembly. 38.3.3 200 mm long, 20 dia rods shall be welded to the pole at 300 mm c/c for access to the device for maintenance purposes. 38.3.4 The support structure shall be hot-dip galvanized. Minimum depth of foundations shall be 1200 mm below GL.
34 | Section-VII(B) - Technical Specifications | 142 of 143 | 6.3 | An Indicative Field & Manufacturing Quality Plan for civil, structural and MMS works is enclosed with this specification for reference as Annexure-E. | An Indicative Field & Manufacturing Quality Plan for civil, structural and MMS works is enclosed with this specification for reference as Annexure-F.
35 | Annexure-A - PG Test Procedure | 3 of 10 | 2.1.1 | Eout - Cumulative AC energy measured at 132 kV Plant End ABT meter over the duration of reporting period (kWh) | Eout - Cumulative AC energy measured at 220 kV Plant End ABT meter over the duration of reporting period (kWh)
36 | Annexure-A - PG Test Procedure | 5 of 10 | 2.1.3.1 | The EPC Contractor shall perform start-up tests after completion of Commissioning and Test Procedure as per Annexure – D: Plant Documentation, Commissioning and Test Procedure and recording of punch points. | The EPC Contractor shall perform start-up tests after completion of Commissioning and Test Procedure as per Annexure – H: Plant Documentation, Commissioning and Test Procedure and recording of punch points.
37 | Annexure-C - Tentative Land Layout with Contour Details | 2 of 2 | - | https://www.dropbox.com/s/b98jw0vaxi2au5h/CPSU%20300%20MW_Ramagiri_Annexure-C_Tentative%20Land%20Layout%20with%20Contour%20Details.dwg?dl=0 | https://www.dropbox.com/s/xdhhwv991oz8sty/CPSU%20300%20MW_Ramagiri_Annexure-C_Tentative%20Land%20Layout%20with%20Contour%20Details_Amended.dwg?dl=0
38 | Annexure-I - Operation & Maintenance Agreement | 4 of 45 | 2.1.2 | In case of failure to meet the functional guarantees as described in section 2.1.1 above, the Contractor shall be liable to pay applicable Liquidated damages as described in the Bid Document and represented in Annexure-2 of this Annexure G. | In case of failure to meet the functional guarantees as described in section 2.1.1 above, the Contractor shall be liable to pay applicable Liquidated damages as described in the Bid Document and represented in Annexure-2 of this Annexure-I.
39 | Annexure-K - Indicative SLD of Interconnecting Substation | - | - | New attachment | Attached
40 | Section-II ITB | 7 of 46 | 5.3 | VOID | The Tender Processing Fee is exempted for MSME Vendors registered under NSIC/ Udyog Aadhaar/DIC Category only
41 | Section-II ITB | 26 of 46 | 32.4.2 Procedure for e- Reverse Auction (e-RA) | 2. After financial bid evaluation, the bidders shall be shortlisted in the ascending order of price bid quoted. Keeping minimum 03 Bids eligible for e-RA, Total no of bids will be reduced by a factor 1/2 and resultant as such, will be eligible for e-RA. Decimal Nos will be corrected to next whole No & will be counted accordingly for the e-RA. If the price bid quoted is same for two or more bidders, then all the bidders with same price bid shall be considered of equal rank/ standing in the order. Ex: (1) No of Bids after arranging the Bids in ascending order = 3, so total No of Bids eligible for e-RA in this case = 3*1/2 = 1.5, but as the minimum 03 bids needs to be kept, so in this case 03 bids will be eligible for e-RA. (2) No of Bids after arranging the Bids in ascending order = 7, so total No of Bids eligible for e-RA in this case = 7*1/2 = 3.5 = 4, rounding off to the next whole No. So, in this case 04 bids will be there for e-RA. In case of substantially low response by the bidders & the total no of responsive bids to be less than 03 (Three), Owner/EMPLOYER reserves the sole discretion & all rights of proceeding/Non-proceeding with e-RA, against the management approval. | 2. After financial bid evaluation, the bidders shall be shortlisted in the ascending order of price bid quoted. Keeping minimum 03 Bids eligible for e-RA, the H1 bidder (bidder with highest EBV) will be eliminated at this stage itself and resultant as such, will be eligible for e-RA. If the price bid quoted is same for two or more bidders, then all the bidders with same price bid shall be considered of equal rank/ standing in the order. In case of substantially low response by the bidders & the total no of responsive bids to be less than 03 (Three), Owner/EMPLOYER reserves the sole discretion & all rights of proceeding/Non-proceeding with e-RA, against the management approval. Evaluated Bid Values (EBV) for all the Bidders shall be compared to determine the lowest Evaluated Bid Value (EBV) as given under Schedule No- 4 Format of Schedule of Rates. Further . The lowest (L1) evaluated Bid as such, will be selected for the Notification of Award (NOA) subject to the successful bidder selected after E-Ra (Clause 32.4.2).
42 | Annexure to BDS | 2 of 7 | 1.1 General Eligibility Conditions | The bidder should be an Indian company registered in India and may be an Affiliate or Holding Company or Subsidiary company of a company meeting the financial eligibility requirement (s) as set forth in this section. Further, Government owned Enterprises registered and incorporated in India are also allowed to participate in this tender. However, the bidders against whom sanction/debarment/blacklisting for conducting business is imposed by Government of India, are not allowed to participate. The subsidiary of a foreign company, which is registered in India under Companies Act, 1956 or 2013 prior to the bid submission deadline, is eligible to participate. | The bidder should be an Indian company registered in India meeting the technical and financial eligibility requirement (s) as set forth in this section. Further, Government owned Enterprises registered and incorporated in India are also allowed to participate in this tender. However, the bidders against whom sanction/debarment/blacklisting for conducting business is imposed by Government of India, are not allowed to participate. The subsidiary of a foreign company, which is registered in India under Companies Act, 2013 prior to the bid submission deadline, is also eligible to participate.
43 | Annexure to BDS | 2 of 7 | 1.1 General Eligibility Conditions | Add following to the existing clause | The Bid Processing Fees and EMD are exempted for MSME bidders registered under NSIC/ DIC/ Udyog Aadhaar Category only. Limited Liability Partnerships, Proprietorships, Partnerships, NGOs, Charitable Trusts, and Educational Societies are not allowed to participate in the bidding process (either individually or in Joint Venture/ Consortium). As the Proprietorships, Partnerships, NGOs, Charitable Trusts, Educational Societies in any form are not allowed to participate in the tendering process, hence any such firm/entity having MSME status is also not eligible to participate in the bidding process (either individually or in Joint Venture/ Consortium).
44 | Annexure to BDS | 4 of 7 | 1.2 Technical Eligibility Conditions | Route III IIIA. The Bidder should have executed in the last ten (10) years an Industrial project either as developer or as EPC Contractor in the area of Power/ Steel/ Oil and Gas/ Petro-Chemical/ Fertilizer/Cement/Coal mining including Coal handling plant and/ or any other process industry, of a value of INR 795 Crores (Indian Rupees Seven hundred & Ninety Five Crores only) or more in a single project or work in a single project or single work respectively and the same should be in successful operation for at least one (1) year prior to the date of techno- commercial bid opening. AND IIIB. The Bidder should have executed at least one (1) Electrical Sub-station of 33 kV or above voltage level, consisting of equipment such as 33kV or above voltage level circuit breakers and Power transformer, either as developer or as EPC Contractor which should be in successful operation for at least one (1) year prior to the date of techno-commercial bid opening. The works referred at clause IIIA & IIIB under Route III above can be in same or different projects. | Route III IIIA. The Bidder should have executed in the last ten (10) years an Industrial project either as developer or as EPC Contractor in the area of Power/ Steel/ Oil and Gas/ Petro-Chemical/ Fertilizer/Cement/Coal mining including Coal handling plant and/ or any other process industry, of a value of INR 223 Crores (Indian Rupees Two hundred & Twenty Three Crores only) or more in a single project or work in a single project or single work respectively and the same should be in successful operation for at least one (1) year prior to the date of techno- commercial bid opening. AND IIIB. The Bidder should have executed at least one (1) Electrical Sub-station of 132 kV or above voltage level, consisting of equipment such as 132 kV or above voltage level circuit breakers and Power transformer, either as developer or as EPC Contractor which should be in successful operation for at least one (1) year prior to the date of techno-commercial bid opening. The works referred at clause IIIA & IIIB under Route III above can be in same or different projects.
45 | Annexure to BDS | 5 of 7 | 1.3 | The bidder should have a minimum Working Capital of INR 111,43,00,000/- (Indian Rupees One Hundred and Eleven crores & forty-three lakhs only) as per the last audited financial statement. If the bidder’s working capital is inadequate, the bidder should supplement this with a letter from the bidder’s bank, having net worth not less than INR 500 Crores, confirming availability of the line of credit for more than or equal to INR 111,43,00,000/- (Indian Rupees One Hundred and Eleven crores & forty-three lakhs only) to meet the working Capital requirement of this particular Project | The bidder should have a minimum Working Capital of INR 74,29,00,000/- (Indian Rupees Seventy Four crores & twenty-nine lakhs only) as per the last audited financial statement. If the bidder’s working capital is inadequate, the bidder should supplement this with a letter from the bidder’s bank, having net worth not less than INR 500 Crores, confirming availability of the line of credit for more than or equal to INR 74,29,00,000/- (Indian Rupees Seventy Four crores & twenty-nine lakhs only) to meet the working Capital requirement of this particular Project
46 | Annexure to BDS | 5 of 7 | 1.3.1 | For participation as an EPC Bidder under Route I: In case the bidder is a subsidiary of a holding company, financial eligibility criteria referred to in clause 1.3 above shall be of that subsidiary company only (i.e. excluding its holding company) | For participation as an EPC Bidder under Route I: In case the bidder is a subsidiary of a holding company, financial eligibility criteria referred to in clause 1.3 above shall be of that subsidiary company only (i.e. excluding its holding company) Bidders participating under Route II and as an Developer under Route III may use the Technical & Financial credentials of their Parent/ Holding/ Subsidiary/ Affiliate/ Group company for qualifying the above-mentioned Technical & Financial qualification requirements as per clause 1.2 and 1.3 respectively. The bidder should be an Indian company registered in India and should be Parent/ Holding/Subsidiary/Affiliate/Group company of a firm meeting the requirement (s) of Clause 1.2 and 1.3 above. In such a case for Route II & Route III, Bidder shall furnish an Undertaking (attached separately with the Pre Bid Clarifications and Amendment 01) jointly executed by the firm qualified as per clause 1.2 and 1.3 and the Bidder along with its bid for complete performance of the contract jointly or severally as per format enclosed in the bid document failing which the Bidder’s bid is liable to be rejected.
47 | Section-IV GCC | 21 of 79 | 19.1 Force Majeure | A ‘Force Majeure’ means any event or circumstance or combination of events those stated below that wholly or partly prevents or unavoidably delays an Affected Party in the performance of its obligations under this Agreement, but only if and to the extent that such events or circumstances are not within the reasonable control, directly or indirectly, of the Affected Party and could not have been avoided if the Affected Party had taken reasonable care or complied with Prudent Utility Practices: • Act of God, including, but not limited to lightning, fire not caused by Bidders negligence and explosion (to the extent originating from a source external to the site), earthquake, volcanic eruption, landslide, unprecedented flood, cyclone, typhoon, or tornado. {Only if it is declared / notified by the competent state / central authority / agency (as applicable)}, • Any act of war (whether declared or undeclared), invasion, armed conflict or act of foreign enemy, blockade, embargo, revolution, riot, insurrection, terrorist or military action, quarantine. • Radioactive contamination or ionizing radiation originating from a source in India or resulting from another Force Majeure Event mentioned above. | A ‘Force Majeure’ means any event or circumstance or combination of events those stated below that wholly or partly prevents or unavoidably delays an Affected Party in the performance of its obligations under this Agreement, but only if and to the extent that such events or circumstances are not within the reasonable control, directly or indirectly, of the Affected Party and could not have been avoided if the Affected Party had taken reasonable care or complied with Prudent Utility Practices: • Act of God, including, but not limited to lightning, fire not caused by Suppliers’ negligence and explosion (to the extent originating from a source external to the site), earthquake, volcanic eruption, landslide, unprecedented flood, cyclone, typhoon, tornado, pandemic and quarantine. {Only if it is declared / notified by the competent state / central authority / agency (as applicable)}, • Any act of war (whether declared or undeclared), invasion, armed conflict or act of foreign enemy, blockade, embargo, revolution, riot, insurrection, terrorist or military action. • Radioactive contamination or ionizing radiation originating from a source in India or resulting from another Force Majeure Event mentioned above.
48 | Section-V SCC | 2 of 12 | 3 | The Time for Commissioning for the cumulative capacity of 300 MW Ground mounted Solar PV Power Plant at Ramagiri along with other associated equipment as per this tender document in total shall be 12 (Twelve) Months from the Date of the Notification of Award NOA/LOA/LOI. | The Time for Commissioning for the cumulative capacity of 300 MW Ground mounted Solar PV Power Plant at Ramagiri along with other associated equipment as per this tender document in total shall be 18 (Eighteen) Months from the Date of the Notification of Award NOA/LOA/LOI.
49 | Section-V SCC | 2 of 12 | 3
50 | Section-V SCC | 5 of 12 | 9 Contract Performance Security | The Contract Performance Security against this Contract need to be furnished as mentioned below: 1. First Stage (Supply and Services): The value of the Contract Performance Security shall be 3% (Three percent) of the Contract Value (i.e., total sum of the Supply & Service Contract). This Performance security will be valid for a total period of 75 Months (12 Months Project commissioning period) + prescribed O & M Period, i.e., 60 Months + 03 Months additional) from the date of its issuance. The successful bidder can submit Contract Performance Security with initial validity of 36 months and the same may be extended after every 36 months till completion of the total 75 months period. | The Contract Performance Security against this Contract need to be furnished as mentioned below: 1. First Stage (Supply and Services): The value of the Contract Performance Security shall be 10% (Ten percent) of the Contract Value (i.e., total sum of the Supply & Service Contract). This Performance security will be valid for a total period of 81 Months (18 Months Project commissioning period) + prescribed O & M Period, i.e., 60 Months + 03 Months additional) from the date of its issuance. The successful bidder can submit Contract Performance Security with initial validity of 36 months and the same may be extended after every 36 months till completion of the total 75 months period.
51 | Section-V SCC | 9 of 12 | 15 Schedule of Rates & Payments | Add following to the existing clause | A payment to be taken through “TReDS” or directly from SECI is a sole discretion of the supplier. SECI shall not intervene in the supplier’s decision to place their invoices on “TReDS” Platform or directly taking payments from SECI. “TReDS” option shall only be given to the MSME supplier and any other supplier “NOT” registered as MSME with SECI, cannot avail this facility.
52 | Section-VI Sample Forms and Formats | - | - | Form of Undertaking by the Bidder and the Firm | New Format attached with the Pre Bid Clarification and Amendment-1
53 | Section - VIII Schedule of Rate | 3 of 3 | - | Add following to the existing clause | 15. Although, its a lumpsum turnkey contract, the line items of the SOR Sheet or the Project BBU prepared on the basis of SOR will be used for the treatment of Change in Law , Payments, Short-Closure, Quantity Variations or for any other reasons not specified here but are in interest of the project.
54 | Annexure to BDS | - | 1.4 Joint Venture & Consortium Conditions | - | "Lead Partner/Member of the JV/Consortium" appearing anywhere in the QR shall be read as "Lead Partner of the JV/Consortium".