## Pre Bid Queries
Tender for Design, Engineering, Supply, Construction, Erection, Testing, Commissioning and O&M of 25 MW (AC) Solar PV Power Plant (50 MWp DC) with 20 MW / 50 MWh Battery Energy Storage System at Taru, Leh, UT of Ladakh, India
Tender No : SECI/C&P/OP/11/014/2024-25
Sl. No. | Tender Section | Page No. | Clause No | Description as per Tender Document | Queries | Category (Finance/Technical/Contractual) | Clarifications
1 | IV | GCC 33 of 80 | GCC 32.1.3 | In the matter of connectivity of Plant to DISCOM’s substation, the Owner will take the necessary connectivity permission, however, all the other permissions and clearances as deemed required by the State Agency/DISCOM for Bay allocation, technical/regulatory compliance for interconnection, ROW etc are to be taken by the Contractor. | As the approval for connectivity is in SECI scope, we request SECI that all the related permissions and clearances as deemed required by the State Agency/DISCOM for Bay allocation, technical/regulatory compliance for interconnection, ROW etc to be in SECI scope. | Contractual | RoW will be in the scope of Contractor. However if required SECI will facilitate the bidder in taking necessary approval and permission from the state agencies/DISCOM.
2 | I | 5 of 223 | - | Design, Engineering, Supply, Construction, Erection, Testing, Commissioning and O&M of 25 MW (AC) Solar PV Power Plant (50 MWp DC) with 20 MW / 50 MWh Battery Energy Storage System at Taru, Leh, UT of Ladakh, India | Bidder requests SECI to reduce the O&M period from 10 years to 5 years, as O&M is a pure service business while being non-core activity for an EPC Contractor. | Contractual | The terms and conditions of the tender document shall prevail.
3 | VI | 352 of 354 | Scheduling and Forecasting | The Contractor shall be responsible for appointing a Qualified Coordinating Agency if required by concerned authorities at the Pooling Substation Level for scheduling and forecasting activity. Also, the contractor shall be responsible for carrying out the forecasting and scheduling of the energy generation from the plant facility (In accordance with the Deviation Settlement Mechanism Regulations of the Jharkhand Electricity Regulatory Commission). Scheduling given by the Contractors is such that no penalty is levied on the Employer due to any deviation of actual generation from scheduling beyond the allowed limit. If any penalty is imposed on the Employer due to such deviations beyond allowed limit the same shall be recovered from the CPS given by the contractor. | Though the Bidder shall follow the best industry practice for Scheduling and Forecasting, but still as the Solar Power generation vastly depends on the weather, which is beyond the control of the Bidder. Hence, the Bidder requests to share the penalty equally between the Bidder and the Employer in case of such penalty imposed by the competent authority. | Contractual | The terms and conditions of the tender document shall prevail.
4 | V | 159 of 223 | SCC 9 | First Stage (Supply and Services): The value of the Contract Performance Security shall be 5% (Five percent) of the Contract Value (i.e., total sum of the Supply & Service Contract). This Performance security will be valid for a total period of 141 Months (18 Months Project commissioning period) + prescribed O & M Period, i.e., 120 Months + 03 Months additional) from the date of its issuance. | We request SECI to modify the clause as : First Stage (Supply and Services): The value of the Contract Performance Security shall be 5% (Five percent) of the Contract Value (i.e., total sum of the Supply & Service Contract). This Performance security will be valid for a total period of 21 month (18 months + 3 months). Further O&M performance BG equal to 5% of O&M contract value shall be valid for 123 Months ( O & M Period, i.e., 120 Months + 03 Months additional) from the date of its issuance. | Contractual | Kindly refer to Amendment 01.
5 | VI | 343 of 354 | ANNEXURE-2 Functional Guarantees | The Contractor guarantees the annual CUF committed herein over the O&M Period (“Annual CUF Guarantee”) from the date of Operational Acceptance. In the event the CUF is less than the Guaranteed CUF, the Contractor shall immediately, upon demand, indemnify the Employer, as liquidated damages and not as penalty, amounts equivalent to remuneration of the equivalent Energy, subject to a maximum of hundred (100%) percent of the Total Annual O&M Price. | Bidder requests SECI to modify the clause as follows: The Contractor guarantees the annual CUF committed herein over the O&M Period (“Annual CUF Guarantee”) from the date of Operational Acceptance. In the event the CUF is less than the Guaranteed CUF, the Contractor shall immediately, upon demand, indemnify the Employer, as liquidated damages and not as penalty, amounts equivalent to remuneration of the equivalent Energy, subject to a maximum of TEN (10%) percent of the Annual O&M Price. | Contractual | The terms and conditions of the tender document shall prevail.
6 | VI | 296 of 354 | 3 | For every 0.01 shortfall in PR below the specified PR value, liquidated damages of 1% of the Contract Value shall be levied. In case the Plant PR Shortfall is more than 0.05 below the specified PR value, then the total plant will be accepted on “as-is basis” & no payments will be made to the contractor pertaining to ‘Operation Acceptance’ milestone in line with the defined payment terms. However, any other earlier pending/running payments as may be applicable, will be paid to the contractor as usual. | Bidder requests SECI to modify the clause as follows: For every 0.01 shortfall in PR below the committed PR value, a LD of 1% of the total Contract Value (i.e., total sum of all the Supply, Service and absolute value of O & M Contract) shall be levied, subject to a maximum of 5% of the overall contract value | Contractual | The terms and conditions of the tender document shall prevail.
7 | IV | 87 of 223 | GCC 2.4.4 | The EMPLOYER/ Owner is not liable for any loss or damage to the Contractor's equipment as a result of variation in voltage or frequency or interruption in power supply or other loss to the Contractor arising therefrom | We shall seek to modify the clause so as to insert that employer shall be liable for any loss/damage that caused due to the act of employer or its men or any third party employed by employer. | Contractual | The terms and conditions of the tender document shall prevail. However all such incidents will be dealt on case to case basis.
8 | IV | 89 of 223 | GCC 6.3 | In all matters concerning the extent of targets set out in the weekly and monthly programs and the degree of achievements the decision of the Engineer-in- Charge will be final and binding on the Contractor. | The decision o of the employer shall not be final and binding. It shall be a mutual decision between employer and contractor. | Contractual | The terms and conditions of the tender document shall prevail.
9 | IV | 98 of 223 | GCC 22.2(a) | the Owner shall also have the right of taking possession and utilizing in completing the works or any part thereof, such as materials, equipment and plants available at work site belonging to the Contractor as may be necessary and the Contractor shall not be entitled for any compensation for use or damage to such materials, equipment and plant | in the event of termination of contract by the employer due to the breach of contractor, contractor shall not be liable for any such usage of the plant of equipment belongs to the contractor by the employer. We shall ask to pay the reasonable payment for the usage of Contractor's equipment/plants | Contractual | The terms and conditions of the tender document shall prevail.
10 | IV | 106 of 223 | GCC 32.1.1 | It is Contractor’s responsibility to coordinate with state/central agencies in order to get any permission whatsoever, required for successful development & operation of Plant till its desired life. | We shall seek:: The permission which is mandatorily be acquired only by the employer has to be acquired by the employer only and contractor shall also be eligible to get any EOTs in case of delay on the part of Employer to get the same. | Contractual | The terms and conditions of the tender document shall prevail. However SECI will facilitate the bidder in taking necessary approval and permission from the state agencies/DISCOM.
11 | IV | 108 of 223 | GCC 33 | Other Agencies at Site 33.1 The Contractor shall have to execute the Work in such place and conditions where other agencies may also be engaged for other works such as site grading, filling, and levelling, electrical and mechanical engineering works, etc. No claim shall be entertained due to Work being executed in the above circumstances. The Contractor shall allow such agencies to use the facilities like roads, etc constructed by the Contractor in order that they are able to carry out their respective scope of works unhindered | it shall be ensured that if any loss or damages caused to contractor due to the act of third parties agencies employed by the employer, the employer shall be liable for the same to the contractor. | Contractual | All such incidents will be dealt on case to case basis.
12 | IV | 111 of 223 | GCC 38.2 | No adjustment in Contract Price shall be allowed for reasons of such delays and extensions granted except as provided in Tender Document, where the EMPLOYER/ Owner reserves the right to seek indulgence of Contractor to maintain the agreed Time Schedule of Completion. In such an event the Contractor shall be obliged for working by Contractor's personnel for additional time beyond stipulated working hours as also Sundays and Holidays and achieve the completion date/interim targets. | We shall seek the compensation to be paid to the contractor, when the contract execution delayed due to the act/omission of the employer. | Contractual | The terms and conditions of the tender document shall prevail. However all such incidents will be dealt on case to case basis.
13 | IV | 114 of 223 | GCC 44 | The provisions of this GCC Clause 44 shall survive termination, for whatever reason, of the Contract | survival of this provision shall not be for indefinite period. We shall seek the definite period . | Contractual | The terms and conditions of the tender document shall prevail.
14 | IV | 117 of 223 | GCC 51 | However, these adjustments would be restricted to direct transactions between the PMC and Contractor and Bought out items (dispatched directly from sub vendor's works to Site). These adjustments shall not be applicable on procurement of raw materials, intermediary components and intermediary services etc. by the Contractor. | We shall seek the adjustment of price in case of statutory variation shall also be applied to procurement of raw materials, intermediary components and intermediary services. | Contractual | The terms and conditions of the tender document shall prevail.
15 | IV | 118 of 223 | GCC 51 | However, any increase in the rate of these taxes, duties and levies beyond the contractual completion period shall be to Contractor's account and any decrease shall be passed on to Owner. | We seek deletion of this clause as any increase /decrease post the contractual completion period shall be borne by respective parties(please consult F&A) | Contractual | The terms and conditions of the tender document shall prevail.
16 | IV | 124 of 223 | GCC 64 | Should any discrepancy occur between the various instructions furnished to the Contractor, his representative or staff or any doubt arises as to the meaning of any such instructions or should there be any misunderstanding between the Contractor's staff and the Engineer-in-Charge/Project Manager's staff, the Contractor shall refer the matter immediately in writing to the Engineer-in-Charge/Project Manager whose decision thereon shall be final and conclusive and no claim for losses alleged to have been caused by such discrepancies between instructions, doubts, or misunderstanding shall in any event be admissible. | the owner decision shall not be final and conclusive, hence we seek deletion of this portion as decision regarding any discrepancies between the instructions has to be resolved mutually by both contractor and owner. | Contractual | The terms and conditions of the tender document shall prevail.
17 | IV | 126 of 223 | GCC 69.1 | Action and Compensation in case of Poor/Non-compliant Work-The decision of the Engineer-in-Charge/Project Manager as to any question arising under this clause shall be final and conclusive. | The decision of the owner shall not be final and conclusive. Hence we seek deletion of this portion. | Contractual | The terms and conditions of the tender document shall prevail.
18 | IV | 127 of 223 | GCC 70.1 | Subject to the provisions of sub-para (ii) of this clause, the Contractor shall, if ordered in writing by the Engineer-in-Charge/Project Manager, or his representative, temporarily suspend the Works or any part thereof for such written order, proceed with the Work therein ordered to be suspended until, he shall have received a written order to proceed therewith. The Contractor shall not be entitled to claim compensation for any loss or damage sustained by him by reason of temporary suspension of the Works aforesaid. However, suitable time extension may be considered at the sole discretion of the owner. | We shall seek : If the work is suspended by the owner other than the fault of contractor, then contractor shall be eligible for the compensation | Contractual | The terms and conditions of the tender document shall prevail. However all such incidents will be dealt on case to case basis.
19 | IV | 127 of 223 | GCC 73.2 | If it shall appear to the Project Manager that any supplies have been executed with unsound, imperfect or unskilled workmanship, or with materials of any inferior description, or that any materials or articles provided by the Contractor for the execution of Contractor are unsound or otherwise not in accordance with the Contract, the Contractor shall on demand in writing inform the Project Manager or its authorized representative specifying the item, materials or articles complained of, notwithstanding that the same may have been inadvertently passed, certified and paid for. The Contractor shall forthwith rectify or remove and replace that item so specified and provide other proper and suitable materials or articles at its own charge and cost, and in the event of failure to do so within a period to be specified by the Project Manager in its demand aforesaid, the Project Manager may on expiry of notice period rectify or remove and re-execute the time or remove and replace with others, the materials or articles complained of as the case may be at the risk and expense in all respects of the Contractor. The decisions of the Project Manager in this regard shall be final and binding. | The decision of the owner shall not be final and conclusive. Hence we seek deletion of this portion. | Contractual | The terms and conditions of the tender document shall prevail.
20 | IV | 130 of 223 | GCC 74 | From the commencement to completion of the Work & till the completion of O&M period (If applicable), the Contractor shall take full responsibility for the care for all works including all temporary works and in case any damages, loss or injury shall happen to the Work or to any part thereof or to any temporary works from any cause whatsoever, shall at his own cost repair and make good the same so that at completion the Work shall be in good order and in conformity in every respects with the requirement of the Contract and the Engineer-in- Charge's instructions. Also damage to external property of Third Parties | We small seek the modification of this clause so as to include that if any loss /damage is happened to work or any part or temporary works due to act/omission/negligent/wilful act of the owner or its men or any third party engaged by owner. Then owner shall be responsible for the same. The contractor shall not be liable for any reason whatsoever. | Contractual | The terms and conditions of the tender document shall prevail.
21 | - | General |  | Suspension by contractor | Please seek addition of the below clause: If Owner fails or delays to release the payments and or perform any other obligations under this Contract, The Contractor may, after giving not less than [21] days’ notice to Ex.Engineer, suspend work (or reduce the rate of work) unless and until the Contractor has received the Payment or the breach of Owner is remedied. The Contractor’s action shall not prejudice its other rights and entitlements including interest on delayed payments. If the Contractor suffers delay and/or incurs Cost as a result of suspending work (or reducing the rate of work), it shall be entitled to : (a) an extension of time for any such delay, if completion is or will be delayed, and (b) payment of any such Costs incurred as a result thereto. | Contractual | The terms and conditions of the tender document shall prevail.
22 |  | General |  | Termination by the contractor | Termination Rights: The Contractor shall be entitled to terminate the Contract if: a) The breach of Owner is not remedied and/or continues despite suspension of contract by the Contractor b) Owner assigns, sublets or transfers this Contract in contravention to the terms of this Contract. c) Owner becomes bankrupt, insolvent, goes into liquidation (voluntary or otherwise), has a receiving or administration order made against him, compounds with his creditors, or carries on business under a receiver, trustee or manager for the benefit of his creditors, an order for corporate insolvency resolution process or liquidation is passed by a court/ tribunal, change of Control, or if any act is done or event occurs which (under applicable Laws) has a similar effect to any of these acts or events. ; Except in events under (c ) where the termination shall be immediate, the Contractor may upon giving 14 days’ notice towner, terminate this Contract in any of the other events listed out hereinabove, without prejudice to its other rights under contract or otherwise; The contractor shall be entitled to: i) return of all performance securities furnished by the Contractor under this Contract ii) payments which shall include: (a) the amounts payable for any work carried out for which a price is stated in the Contract; (b) the Cost of Plant and Materials ordered for the Works which have been delivered to the Contractor, or of which the Contractor is liable to accept delivery; (c) any other Cost or liability which in the circumstances was reasonably incurred by the Contractor in the expectation of completing | Contractual | The terms and conditions of the tender document shall prevail.
23 | Section - VII Technical Specification | 7 of 354 | 1 | 66 kV Loop-in-Loop-out (LILO) in 66 kV I/C line from Phyang S/s to 66 kV O/G line to Leh S/s Tower No: From 326 to 325 | Please provide the coordinates of tower no. 325 and 326. | Technical | Please refer Specific Annexure: SA-A, site layout along with coordinates have been provided. .dwg file is also being provided.
24 | Section - VII Technical Specification | 6 of 354 | 1 | Latitude & Longitude Refer Specific Annexure-SA-A: Tentative Land Layout Available Land Area | Please provide the kmz file of the location. | Technical | Please refer Specific Annexure: SA-A, site layout along with coordinates have been provided. .dwg file is also being provided.
25 | Section - VII Technical Specification | 7 of 354 | 1 | Project Particulars BESS availability - 95% | Please provide confirmation regarding the discrepancy concerning the availability of BESS. | Technical | Kindly refer to Amendment 01.
26 | Section - VII Technical Specification | 111 of 354 | 3 | Technical specification of battery energy storage system- BESS availability - 98% |  | Technical | Please refer Amendment-1 (S.No.1)
27 | Section - VII Technical Specification | 111 of 354 | 3 | Battery Technology - Any battery technology with totally Maintenance Free suitable for operation in site-specific climatic conditions can be used. | Bidder will be proposing Li-ion battery. Please accept. | Technical | Li-Ion battery technology is acceptable, subject to the specifications provided in the tender. Terms & Conditions of Tender shall prevail.
28 | Section - VII Technical Specification | 111 of 354 | 3 | System ac-dc-ac efficiency*: >80% | Bidder understand that the indicated system efficiency is exclusive of auxiliary consumption. | Technical | Please refer Clause 6.6 of SUB-SECTION D GENERAL ANNEXURE I Plant Documentation, Commissioning & Test Procedure
29 | Section - VII Technical Specification | 111 of 354 | 3 | Energy rating - Minimum 50 MWh Nameplate capacity with at least 40 MWh dispatchable at the beginning of life and not less than 80% of this capacity i.e. 32 MWh at any point of time up to End of Battery Life. | Bidder understand that 40MWh is required at 11kV point of interconnection and point of metering at beginning of life. Please confirm. Minimum 32MWh is required at end of life. Please confirm which year to be considered as end of life. Employer to clarify if augmentation is allowed? | Technical | Yes, BESS dispatchable capacity shall be as measured at the Point of metering of the BESS feeder. Please refer Clause 6.6 System Rating Verification under GENERAL ANNEXURE I: Plant Documentation, Commissioning & Test Procedure along with S. No. 17 of Amendment. End of Life: Please refer Cl. 4.4 (TS-Electrical-B(BESS) for Design Life of BESS. Please also refer Amendment S. No. 16 of Amendment for year-wise minimum dispatchable capacity. Augmentation: Augmentation is not allowed.
30 | Section - VII Technical Specification | 111 of 354 | 3.1 | Minimum 50 MWh Nameplate capacity with at least 40 MWh dispatchable at the beginning of life and not less than 80% of this capacity i.e. 32 MWh at any point of time up to End of Battery Life. | Clause 3.1 specifies the need for 20MW of power with a dispatchable capacity of 40MWh, taking into account a discharge rate of 0.5C. However, in clause 3.4.1, it states that we should consider 4 hours of discharge, which would increase the dispatchable capacity to 80MWh. Employer to clarify this apparent discrepancy? | Technical | Required Dispatchable BESS capacity is 40 MWh as measured at POC mentioned in Scope of Works with a maximum discharge rate of 0.5C. However, discharge for 4 hours @ 10MW of Power shall be considered for Auxiliary power considerations during the detailed engineering.
31 | Section - VII Technical Specification | 112 of 354 | 3.4.1 | Note: For the purpose of system nameplate sizing subject to the minimum specified in Table 2: Supply-Specific Ratings and Requirements above, the Contractor shall consider 4 hours of discharge during the post-solar hours. |  | Technical
32 | Section - VII Technical Specification | 113 of 354 | 4.4 | Design Life and Life-Cycle Costs: End of battery life – End of battery life is that point in time when the BESS can no longer meet the power and/or energy discharge requirements of this Specification due to age or non-repairable malfunction of the accumulation subsystem, and/or non-replaceable components. When the system is no longer able to provide these requirements, the system has reached its end of life. Battery End of life shall not be less than the total period from the date of Commissioning to the expiry of the O&M contract | Bidder request to confirm the year to be considered as end of life to optimize the battery sizing. | Technical | End of Life of BESS co-incised with the period of O&M Please refer Cl. 4.4 (TS-Electrical-B(BESS) for Design Life of BESS
33 | Section - VII Technical Specification | 116 of 354 | 4.7.13 | Unit battery monitoring, whether automatic or manual, should be specified to alert the proper personnel in a timely manner that an abnormal unit battery condition exists or may exist. All alarms shall be part of the control system and shall include remote display or annunciation capability. | Bidder request to accept the BESS Rack level monitoring capabilities(Includes min and max cell voltage and temp information) over remote server. | Technical | The terms and conditions of the tender document shall prevail.
34 | Section - VII Technical Specification | 119 of 354 | 4.11.3 | Auxiliary Power Auxiliary System shall provide for whatever emergency power backup is necessary for orderly shutdown during abnormal conditions such as loss of grid power. | Employer to clarify duration of the power backup requirement. Bidder will consider auxiliary load of solar and BESS. | Technical | In addition to the auxiliary load of Solar and BESS during normal operation, the Contractor shall identify the requirement of additional backup power required for orderly shutdown as per the OEM requirements.
35 | - | - | - | General | Bidder request to Kindly accept the flexibility of laying the cables as directly buried or open air cable tray for the BESS system. Please accept. | Technical | Accepted.
36 | - | - | - | General | Employer to provide the anti-corrosion category for Battery energy storage system. | Technical | The Contractor shall propose corrosion protection requirements as per the site conditions.
37 | - | - | - | General | Employer to confirm that how much percentage of solar power generation can be utilised for battery charging. Also employer to confirm that the priority is BESS charging or grid dispatch? | Technical | Grid Dispatch shall be given first priority. The Contractor shall guarantee Annual CUF as per the tender specifications. It is as per contractor's design to decide the percentage of Generation to charge to meet the Annual CUF guarantee while dispatching max energy through BESS in the non-solar hours.
38 | - | - | - | General | Employer to provide ERT, soil thermal resistivity report. | Technical | All site investigations are in the Scope of the Contractor. However, Geotech Investigation Report along with the ERT Results are enclosed as Specific Annexure : SA-D Geotechnical Investigation Report for Reference purposes only.
39 |  |  |  |  | Bidder request you to share Year on Year degradation. |  | Please refer Clause 1.5.1 - Performance Warranty for PV Module degradation warranty conditions.
40 | Section - VII Technical Specification | 6 of 354 | 1 Project Particulars | Module Technology Mono-Crystalline PERC / TOPCon | Bidder request to add thin film module technology with less than 530 Wp along with mono crystalline & Top con. | Technical | Kindly refer to Amendment 01.
41 | Section - VII Technical Specification | - | - | - | Kindly Clarify the BESS Integration point with Solar plant . Also please provide the BESS Integration SLD for better understanding | Technical | The BESS will be coupled with the PV System at the AC Bus on the MV (11 kV) side of the Inverter Transformers. Please refer Cl. 2.1 (TS-Electrical (B-BESS),
42 | General | - | - | General | Kindly confirm requirement of grid limitation at Point of interconnection. | Technical | Grid Limitation is 25 MW, which is the Project Capacity.
43 | Section - VII Technical Specification | 6 of 354 | 1 Project Particulars |  | Bidder understands, that DCR Category modules only to be considered for this tender | Technical | PV Modules shall conform to MNRE Order on Public Procurement (Preference to Make in India) to provide for Purchase Preference (linked with local content) in respect of RE Sector dated 9th February, 2021 and subsequent amendments . Please refer Clause 1. Project Particulars - Origin of Supply Items.
44 | Section - VII Technical Specification | 6 of 354 | 1 Project Particulars | Project AC Capacity 25 MW Cumulative Power Transformer Capacity 50 MVA (2 X 25 MVA) Cumulative Inverter Duty Transformer Capacity 40 MVA Cumulative Inverter AC Capacity 40 MVA Note: Inverter shall be capable of delivering 25 MW AC Power with PF range -0.95 to +0.95 at POI DC Capacity 50 MWp | Kindly clarify the project ac capacity, inverter capacity and IDT capacity. | Technical | Project Capacity: 25 MW (AC) Inverter Capacity: Min. 40 MW IDT Capacity: 40 MVA
45 | Section - VII Technical Specification | 6 of 354 | 1 Project Particulars | Cumulative Inverter AC Capacity 40 MVA Note: Inverter shall be capable of delivering 25 MW AC Power with PF range -0.95 to +0.95 at POI | Kindly clarify the temperature and altitude , inverter shall be designed. | Technical | Please refer Design Parameters, in Clause 1, Scope of Works. Please refer Specific Annexure: SA-A for location coordinates.
46 | Section - VII Technical Specification | 31 of 354 | 4 Power Conditioning Unit | The rated/ name plate AC capacity of the PCU shall be AC power output of the PCU at 25°C. |  | Technical
47 | Section - VII Technical Specification | 7 of 354 | 1 Project Particulars | Plant End Substation Power Transformer Capacity 50 MVA (2 X 25 MVA) Plant End Substation Switching Scheme (66 kV) Double Bus Scheme (Main Bus-I & Main Bus-II) Point of Interconnection 66 kV Loop-in-Loop-out (LILO) in 66 kV I/C line from Phyang S/s to 66 kV O/G line to Leh S/s Tower No: From 326 to 325 | Bidder request to provide typical SLD for the POI. | Technical | Point of Interconnection shall be LILO arrangement at Tower Nos. 326 to 325. The detailed design and engineering for shall be in the scope of the Contractor, in line with the requirements of Leh-PDD.
48 | Section - VII Technical Specification |  |  |  | Kindly clarify the termination point and scope of bidder. | Technical
49 | Section - VII Technical Specification | 7 of 354 | 1 Project Particulars | Minimum Guaranteed Generation During O&M period 36.1% | 1. Kindly elaborate on the minimum generation guarantee. Also clarify whether guarantee is for solar power plant or BESS. 2.Bidder understands that the Pac given in the formula is the Plant AC capacity i.e. 25MW 2. As BESS Integration involved in this project, Bidder requests to change the metering point to solar side only for CUF Calculation instead of Plant End Metering | Technical | 1. Please refer Amendment-1 (S.No.3) & read it as "Minimum CUF Guarantee". It shall be applicable at Plant End Metering Point. 2. Yes. 3. Guaranteed CUF is after BESS losses. CUF shall be calculated at the Plant End Metering point.
50 | GENERAL ANNEXURE J Functional Guarantee (FG) Test Procedure | 292 of 354 | 2.12 Performance ratio |  | According to the provided formula, the performance ratio has not met the required PR of 87% for some months without grid limitations. Considering the grid limitation, it is anticipated that the PR won't be achieved. The bidder requests to reconsider the performance ratio less than 78%. | Technical | Kindly refer to Amendment 01.
51 | Section - VII Technical Specification | 31 of 354 | 4 Power Conditioning Unit | Type-I+II surge protective device (SPD) conforming to IEC 61643-31 shall be connected between positive/ negative bus and earth on the DC side. Type-II SPD conforming to IEC 61643-11 shall be provided on the AC side. | Bidder request to consider Type II SPD for DC and AC side of PCU. | Technical | The terms and conditions of the tender document shall prevail.
52 | Section - VII Technical Specification | 23 of 354 | A Electrical System 1 Photovoltaic Modules | Rated power at STC ≥ 540 Wp, No negative tolerance is allowed | Bidder request to choose module with rated power lower than 540 Wp. As total DC capacity shall be 50MWp anyway. | Technical | Kindly refer to Amendment 01.
53 | Section - VII Technical Specification | 23 of 354 | A Electrical System 1 Photovoltaic Modules | Module Efficiency ≥ 20.9 % | Bidder request to reduce the module efficiency limit by 1%. | Technical | The terms and conditions of the tender document shall prevail.
54 | Section - VII Technical Specification | 63 of 354 | 13 Lightning Protection System | 13.2 Protection level for the entire plant shall be Level-III. | Bidder request to consider lightning protection level for the entire plant to be level - 4 | Technical | The terms and conditions of the tender document shall prevail.
55 | Section - VII Technical Specification | 63 of 354 | 13 Lightning Protection System | 13.4 Necessary foundation/anchoring for holding the air terminal in position to be made after giving due consideration to shadow on PV array, maximum wind speed and maintenance requirement at site in future. | Bidder understands that there is no need for removal of PV array in the ESE LA shadow area since it is moving shadow. | Technical | PV arrays are not to be placed in the LA Shadow area.
56 | GENERAL ANNEXURE J Functional Guarantee (FG) Test Procedure | 295 of 354 | 2.1.4 PG Test Procedure | The Functional Guarantee condition for the purpose of Provisional Acceptance of the Plant Facilities shall be considered to have been met if the average of daily PRs (for 30 days*) is greater than or equal to the guaranteed Performance Ratio (PR). | As the PR will vary according to month. Bidder request consider the PR for PR test as per the monthly PR values, which can be submitted during detailed engineering time or during bid submission. | Technical | Kindly refer to Amendment 01.
57 | Annexure - A PG Test Procedure | 344 of 354 | 1. Annual CUF Guarantee | Reference Irradiation for the site = 1827 kWh/m2/year | Kindly share the reference for the 1827 kWh/m2/year or kindly confirm the meteo source to be used for performance guarantee (Meteonorm/Solargis). | Technical | SolarGIS LTA GHI has been used as the reference GHI.
58 | General | - | - | General | It is understood that the soil is collapsible in nature due to boulder available up to 10 m depth, We request SECI to provide soil test report in order to analyze the soil condition and design foundations appropriately. | Technical | Geotech Investigation is in the scope of the Contractor. Summary details have been provided in the Annexure SA-B - General Site Information.
59 | General | - | - | General | Bidder understands that there is no need for removal of PV array in the Transmission line(String) shadow area since it is moving shadow. | Technical | PV Arrays are not to be placed in the 66 kV HT Line corridor identified in the Annexure SA-A: Tentative
60 | General | - | - | General | Bidder considering unavailability to be 0.5% as per standard practice for Solar | Technical | The Contractor may consider unavailability as per design. It may be noted that duration of Grid Unavailability is excluded from the calculation of CUF.
61 | General | - | - | General | M/s SECI kindly share the AutoCAD drawing of the vicinity map. Also kindly share the Topography map, Hydrology report, Soil report and also kmz file for the plots used in this Project. | Technical | Layout of the project area with corner coordinates have been readily shared with the tender. All relevant investigation shall be in the scope of the bidder. Please refer Amendment S. No. 18 for updated Annexure SA-A : Site Layout
62 | General | - | - | General | M/s SECI Kindly provide the corrosion category for the plant to be considered | Technical | Minimum requirements of corrosion protection, where applicable have been provided in the TS.
63 | General | - | - | General | M/s SECI Kindly provide the wind speed for the plant to be considered | Technical | Please refer Cl.1 (Design Parameters) of Scope of Works
64 | Foundations (General) | 154 of 354 | 11 | Foundations (General)-Min. depth of foundation for all buildings and plinth for open installations shall be 1.5 m below NGL. Min. depth of foundation for steps in brick and concrete masonry shall be min. 450mm below FGL. For all other structures, min. depth of foundation shall be 1.0 m unless specified otherwise. | Bidders proposes to chose the Foundation size and depth depending on the Geotech report and as per design requirement inline to site conditions and therefore there may be variation in foundation quantity. | Technical | Accepted subject to the minimum criteria specified in this Clause.
65 | CHAIN LINK FENCE DRAWING | 267 of 354 |  | General | Bidder can allow road crossings from one plot to another plot through the transmission corridor, kindly confirm | Technical | Yes, road crossing from one plot to another plot through the transmission corridor are acceptable subject to the road arrangement meeting the minimum clearance requirements for the transmission line.
66 | Specific annexure B | 301 of 354 | 3 | The possibility of encountering weakened bridges that may limit the quantum of transport, in addition to the consideration of navigating through sharp turns and narrow valleys in their logistics strategy as regards to vehicle type and weight transported, shall also be considered by the EPC contractor. | M/s SECI Kindly provide the details available and location of weakened bridges | Technical | Details not available with the Employer. The Bidder shall carry out logistics survey for requisite information.
67 | 5 Inverter Transformer and Auxiliary Transformer | 35 of 354 | 5.2 Technical Requirements | Inverter Duty Transformer (Winding material) | Winding material details for IDT is not mentioned in RFP. Bidder request to allow the Aluminium winding for IDT. Kindly confirm your acceptance for the same. | Technical | Aluminium winding for IDT is acceptable.
68 |  |  |  | Inverter Duty Transformer (Losses) | Losses details for IDT is not mentioned in RFP. Bidder request to accept the total losses (NL+FLL) up to 1.1%. Kindly confirm your acceptance for the same. | Technical | Total IDT Losses have not been specified. The Contractor shall propose equipment losses during detailed engineering to meet the guaranteed CUF requirement at the Point of Metering.
69 |  |  |  | Inverter Duty Transformer (Insulating oil) | Insulating oil details for IDT is not mentioned in RFP. Bidder understand mineral oil can be used for IDTs. Kindly confirm your acceptance for the same. | Technical | Transformer Insulating Oil shall be as per IS 335, IEC 60296. Please refer Clause 5.1 Standards and Codes
70 |  |  |  | Tap Changer-OCTC, No. of steps shall be as per system requirement | Bidder understand OCTC +/-5% required on 2.5% steps. Please confirm the same. | Technical | Accepted.
71 | 6 11 kV HT Switchgear Panel | 41 of 354 | 6.2 Technical Parameters | Internal Arc Classification - IAC-A, FLR, 25 kA for 1s | Bidder requests the internal arc type tested panel shall be applicable for indoor type panels only. This is not applicable for outdoor type panels placed in inverter Platform. | Technical | The terms and conditions of the tender document shall prevail.
72 |  |  |  | Current Transformer Accuracy class - 0.2 for metering (0.2S for metering at outgoing feeder), 5P20 for protection | At ICR Level ICOG, CT Accuracy class will be 0.5 and at MCR HT Switchgear shall be 0.2 (incomer PV and BESS feeder) & 0.2s for metering (outgoing Feeder). Please confirm | Technical | The terms and conditions of the tender document shall prevail.
73 |  |  |  | Voltage Transformer : 0.2 for metering, 3P for protection | At ICR Level ICOG, PT Accuracy class will be 0.5 and at MCR HT Switchgear shall be 0.2 (incomer PV and BESS feeder) & 0.2 for metering (outgoing Feeder). Please confirm | Technical | The terms and conditions of the tender document shall prevail.
74 | 6.3 Switchgear Panel | 42 of 354 | 6.3.3 | The panel enclosure shall be constructed with CRCA steel/Aluzinc sheet. The thickness of load bearing members shall be minimum 3 mm and that of non-load bearing members shall be minimum 2 mm. | Switchgear Panel material & thickness will be as per OEM type tested design Only. | Technical | Switchgear Panel material & thickness will be as per OEM type tested design, subject to the minimum thickness specified herein.
75 | 7 AC Cables | 49 of 354 | 7.2 | All AC cables shall be flame retardant, low smoke (FRLS) type designed to withstand all mechanical, electrical and thermal stresses develop under steady state and transient operating conditions. | Please confirm FRLS required for all AC cables. ? | Technical | Yes. The terms and conditions of the tender document shall prevail.
76 |  | 50 of 354 |  | AC Cables | Details of cable conductor material type is not available in RFP. Bidder request to considered Aluminium cables for all type of cables. Kindly provide your acceptance. | Technical | Accepted
77 | 8 Auxiliary Supply System | 51 of 354 | 8.3 | Auxiliary supply system | 1. Bidder understand 1 x 100% auxiliary transformer required at Main control room same shall be taped from 11 kV HT switchgear. 2. Auxiliary transformer requ. Is not specified for ICR room. bidder understand 1 x 100% auxiliary transformer required at inverter control room same shall be taped from LV side of IDT kindly provide your confirmation for the acceptance of the same. | Technical | Auxiliary Supply system design shall be finalised during detailed Engineering design
78 |  |  |  | Auxiliary system of Pooling Substation shall incorporate redundant source of power supply for increased reliability. | Bidder will offer Common Auxiliary supply system for both Switchyard and CMCS. | Technical | The terms and conditions of the tender document shall prevail. Auxiliary Supply system design shall be finalised during detailed Engineering design
79 |  |  | 8.4 | Following consideration shall be taken into account while sizing the auxiliary transformer: (i) 20% future load margin (ii) Total connected load at 0.8 power factor | Bidder understand 10 % margin is sufficient for auxiliary transformer at MCR & ICR both. Kindly provide your confirmation for both. | Technical | The terms and conditions of the tender document shall prevail.
80 | 9 LT Switchgear | 53 of 354 | 9.3 | LT switchgear - Constructional Details | Bidder request to have consideration for Aluminium bus bar. Kindly confirm your acceptance for the same. | Technical | The terms and conditions of the tender document shall prevail.
81 |  | 54 of 354 | 9.3.13 | Earth leakage relay with Core balance CTs (CBCT) shall be provided on main incoming feeders having phase CT ratio more than 50/1A. | Bidder propose MCCB with LSIG for earth fault protection instead of CBCT to provide the leakage protection in the LV panels. Please provide your acceptance for the same. | Technical | The terms and conditions of the tender document shall prevail.
82 | 10 Uninterrupted Power Supply | 55 of 354 | 10 | Uninterrupted Power Supply | Bidder Understand that 1X100% UPS is required at the Inverter and MCR both area. Kindly confirm. | Technical | Shall be finalised during detailed Engineering design.
83 |  | 56 of 354 | 10.3.2 | Type - Sealed, Maintenance-Free (AGM) battery | Bidder request to allow SMF VRLA batteries. Kindly provide your confirmation for same. | Technical | The terms and conditions of the tender document shall prevail.
84 | 11 Battery and Battery Charger | 57 of 354 | 11 | Battery and Battery Charger | Bidder Understand that 1X100% Battery charger with 1X100% Battery is required at MCR, However, Battery charger at ICR is not required, UPS shall be cater the backup requirement at ICR. Kindly confirm. | Technical | Shall be finalised during detailed Engineering design.
85 | 12 Earthing | 60 of 354 | 12.2.2. | The earth electrode shall be made of high tensile low carbon steel rod, molecularly bonded by high conductivity copper on outer surface with coating thickness not less than 250 micron as per relevant standards. | Bidder request to consider the mild steel rod for earthing Kindly confirm your acceptance for the same. | Technical | The terms and conditions of the tender document shall prevail.
86 | 13 Lightning Protection System | 63 of 354 | 13.2 | Protection level for the entire plant shall be Level-III. | Bidder request to allow the Level-IV protection. | Technical | The terms and conditions of the tender document shall prevail.
87 | 16.2 Functional requirements | 165 of 354 | 16.2.2 LCR/ICR | Building for installing inverter and associated equipment shall be of PEB (Pre-engineered building) type or RCC framed structure. | Bidder request to allow for outdoor type Inverter control room RCC based platform under the shed. All equipment such as Inverter, HT panel, UPS with Battery bank and auxiliary supply equipment shall be kept on the same under shade. | Technical | Kindly refer to Amendment 01.
88 | 19.3 Relays | 87 of 354 | 19.3.15 | Each feeder shall have two lock out relays powered through two independent DC supplies. Each lock out relay shall send through two separate potential free output contacts signals to each of the two independent trip coils. | Bidder is proposing that each feeder will have only one Lock Out relay with one independent DC supply. | Technical | The terms and conditions of the tender document shall prevail.
89 | 21 Illumination | 98 of 354 | 21.2.1 | This specification covers design, supply and installation of uniformly Illumination system along the peripheral corridor, access & internal roads, main control room & inverter rooms, switchyard and other facilities including entry points/gate(s) inside the plant area. | Bidder propose lighting pole shall be provided near to inverter station and periphery only, Internal road light is not required to avoid the shadow impact on the modules | Technical | The terms and conditions of the tender document shall prevail.
90 |  |  | 21.3.1 | Lighting Levels Internal / Access Roads - 4 Lux. | Bidder understand the average 4 lux to be maintained for peripheral roads. Please provide your acceptance for the same. | Technical | Accepted. Average 4 lux shall be maintained for peripheral roads.
91 | 21.3 Lighting Levels |  |  | Control Room and equipment rooms - 300 Lux Office - 300 Lux | Bidder proposes Lux level for SCADA and Admin rooms shall be avg 250 lux and rest rooms in MCR shall be 100 Lux. | Technical | The terms and conditions of the tender document shall prevail.
92 | Project Particulars | 6 of 354 | Design and Engineering | Project AC Capacity - 25 MW Cumulative Power Transformer Capacity - 50 MVA (2 X 25 MVA) Cumulative Inverter Duty Transformer Capacity 40 MVA BESS Power Rating 20 MW | Please clarify the below point 1. Project AC Capacity is 25 MW only, but the Cumulative Inverter Duty Transformer capacity is 40 MVA. 2. For 25 MW Solar Plant, Cumulative Power Transformer Capacity is 50 MVA (2 X 25 MVA). | Technical | 1. Yes, cumulative IDT Capacity (Solar Part) is 40 MVA. 2. Yes
93 | General | - | - | General - Plant AC SLD. | Tender SLD is not available in RFP. Kindly share the same. | Technical | Plant Design SLD is in the Scope of the Contractor. The same shall be finalised during detailed engineering
94 | General | - | - | General - MCR Layout Plan | MCR layout plan is not available in RFP. Kindly provide the same with minimum requirement to be maintained for the MCR. | Technical | Minimum areas for the MCR Building have been specified in the Tender Specifications. Layout preparation is in the Scope of the Contractor. The same shall be finalised during detailed engineering.
95 | General | - | - | General | Bidder understands that Radial scheme is allowed from the ICR to MCR feeder where two separate ICOG/HT panels (each 13.2MW max) capacity shall directly connected to single VCB vertical (26.4MW capacity) at MCR MV switchgear panel. | Technical | The terms and conditions of the tender document shall prevail.
96 | General | - | - | General | Kindly confirm the corrosion category to be considered for the equipment's. | Technical - Civil | Minimum requirements of corrosion protection have been laid out in the TS.
97 | General | - | - | General - Short circuit withstand capability for cable. | Cable short circuit withstand will be sized as per Relay coordination study. Please confirm | Technical | Agreed
98 | General | - | - | General | Kindly confirm the ERT value to be considered at the preliminary stage. | Technical | Detailed Geotechnical investigation is in the scope of the Bidder.
99 | General | - | - | General | Proposed SCADA system shall withstand 0 to 50°C for the equipment in SCADA main control room and -20°C to +50°C for the equipment in Inverter control room. Kindly confirm | Technical | SCADA design parameters shall be as per design ambient temperature specified in the Clause 1. Project Parameters.
100 | 4 Procurement & Supply | 12 of 354 | 4.12 | 66/11 kV Plant Pooling Substation with required number of 11 kV bays, required no. of 66/11kV transformers, four nos. of 66 kV Bays (Two Transformer Bays, One Line Bay & One Bus Coupler Bay), Bus PTs. Busbars, Equipment of Line Bay and Bus Coupler Bay shall be suitable for evacuation of 25 MW. | Bidder understand that at point of Interconnection 66 kV LILO system is required with two Line bays each bay for Line In And Line Out but as per RFP clause No. 4.12 Only One Line bay requirement is mention please clarify the same. | Technical | Kindly refer to Amendment 01.
101 |  |  |  | Rated short circuit current @ 66KV | Bidder understand that short circuit rating for the all switchyard equipment at 66kV PSS shall be consider as per the CEA latest guideline is 31.5 kA . | Technical | It shall be as per the system requirement.
102 | General | - | - | General - Switchyard SLD | Tender SLD is not available in RFP. Kindly share the same with required busbar rating. | Technical | Switchyard SLD is in the Scope of the Contractor. The same shall be finalised during detailed Engineering.
103 | Technical Specification-Section VII | 65 of 354 | 15-SCADA -15.2.1-Architecture | The SCADA System shall be built over Industrial IoT architecture with integrated Analytics, secure web access, enterprise software and Database. | Bidder requests to accept the option of having PLC processor based architecture for SCADA design. Bidder wants to inform that, PLC processor based architecture is commonly used in Solar projects. Kindly provide your acceptance for the same. | Technical | The terms and conditions of the tender document shall prevail.
104 |  | 66 of 354 | 15-SCADA -15.3-Industrial IoT Controllers & Data Acquisition | The Plant SCADA and Monitoring System may use one or more IIoT Controllers at each Inverter Control Room and MCR for the purpose of data acquisition and data forwarding to the SCADA Servers.
105 | Technical Specification-Section VII | 65 of 354 | 15.2.7 | Operator Workstation/PC shall be of Industrial Grade for browser-based access to plant data from Plant. Plant control & SLDC/Utility related operations shall only be initiated through browser-based interface requiring no client software or database to be installed on the Workstation | Bidder wishes to clarify that, As the SCADA OEM's (Vendors) works on independent methodology as per their System design, Browser based interface / Server-Client based design / any other applicable as per technical needs, shall be finalized during detailed engineering based on SCADA vendor recommendation to meet the SCADA specifications. Kindly provide your acceptance for the same | Technical | The terms and conditions of the tender document shall prevail.
106 | Technical Specification-Section VII | 68 of 354 | 15.5.6 | The SCADA system shall have user-friendly browser-based User Interface for secure access from anywhere, for minimum ten concurrent connections from the Operator PC or other securely connected laptop/mobile, for plant monitoring, O&M, daily reporting, and analysis | Bidder requests client to confirm the exact requirement of Quantity (Nos) of 1. Browser (i.e. Laptop) based user access and 2. Mobile user licenses Kindly confirm. | Technical | Bidder may consider as following: 1. Browser based user access - 7 Nos. 2. Mobile User licenses - 3 Nos.
107 | Technical Specification-Section VII | 69 of 354 | 15.7.1 | All RS485, IO and CAT6 cables shall be laid in separate conduits with a minimum separation of 1.5ft from AC/DC power cables all along. | a. Bidder wishes to clarify that as RS 485 and IO cables are armoured cables, Conduits are not required. Hence we propose not to consider conduits for armoured communication and IO cables. b. As per IS 1255 standard, it is specified that, 300 mm (1 foot) clearance can be provided between Power and Communication cables, and hence the same can be followed for all communication & Instrumentation IO cables. Kindly provide your acceptance for the same. | Technical | The terms and conditions of the tender document shall prevail.
108 |  |  | 15.7.2 | Power cables shall be laid deep in the trenches first. Data cables shall be laid in separate conduits after partially filling the trenches to ensure minimum 1.5 ft separation between power and communication cables all along the trench |  | Technical
109 |  |  | 15.7.3 | IO Cables between switch gear panels and SCADA panel shall be laid on separate cable trays, with a minimum of 1.5ft separation from trays carrying AC Power cables. |  | Technical
110 |  |  | 15.7.4 | RS485 & CAT6 cables between switch gear panels or Inverters and SCADA panel shall be laid on separate cable trays, with a minimum of 1.5ft separation from trays carrying AC Power cables. |  | Technical
111 | Technical Specification-Section VII | 70 of 354 | 15.10.2 | Operating System and Database shall be of enterprise scale (RedHat Linux or equivalent Linux OS, Oracle/MySQL or Windows or equivalent DB), with required AMC for 5 years | Bidder proposes that, it is recommended to consider Windows Server Operating System for Plant server as Windows Operating system is compatible for all standard SCADA software's. As per the Operator Workstation specifications, it is mentioned to consider Windows operating system, hence for integration of Plant Server and Operator Workstation, Bidder recommends to consider Windows based operating system for both Plant server and Operator Workstation. Kindly provide your acceptance for the same. | Technical | Kindly refer to Amendment 01.
112 | Technical Specification-Section VII | 70 of 354 | 15.10.2 | PPC Workstation-1 | Bidder wishes to clarify that separate PPC workstation is not required . All the PPC data shall be monitored and interfaced in the SCADA Workstation itself. However dedicated PPC panel and PPC controller shall be considered. | Technical | The terms and conditions of the tender document shall prevail.
113 | Technical Specification-Section VII | 100 of 354 | 22.1.2 & 22.3 | Ingress protection -Pyranometer IP67 and Anemometer-IP66 | Bidder quotes that for Pyranometer and anemometer the ingress protection of IP65 is sufficient | Technical | The terms and conditions of the tender document shall prevail.
114 | Technical Specification-Section VII | 102 of 354 | 23 .1 | CCTV Cameras along with monitoring stations (sufficient numbers) and all other accessories required for its proper operation must be installed to have complete coverage of following areas for 24 hours. (ii) Along the Plant Perimeter: Covering complete perimeter of Plant Area to capture all possible intrusion | Bidder wishes to clarify that for solar power projects, CCTV at entire plant perimeter is not required . CCTV camera shall be considered only at strategic locations as specified in the RFP. Please confirm your acceptance for the same. | Technical | Kindly refer to Amendment 01.
115 | Technical Specification-Section VII | 130 of 354 | Energy management system | Complete clause | Bidder understands that, Energy Management System specifications mentioned are same as Power Plant Controller (PPC) which is used in Solar projects, hence we need to consider PPC to meet EMS requirements. Kindly confirm the same. | Technical | Yes. PPC specifications specified in Clause 16 shall meet the functional requirements provided for EMS.
116 | Technical Specification-Section VII | 294 of 354 | 2.1.4 | Before the commencement of PG test, the plant shall have completed Pre-PG tests as per Clause 2.1.1 above and SCADA system and WMS shall be fully commissioned and functional. | Bidder understands that one datalogger is sufficient for conducting the PG Test of both SCADA & WMS | Technical | As specified in the Clause, the plant SCADA and WMS shall be fully commissioned and functional prior to commencement of PG Tests. Data for PG Tests shall be available from the SCADA system.
117 | I | 3 of 11 | 1.4 | The Lead partner of the JV/Consortium shall meet individually 100% of Technical Eligibility Conditions given at para 1.2 above. | Lead bidder can be a system integrator | Contractual | The terms and conditions of the tender document shall prevail.
118 | III | 2 of 10 | 3.2 | Date of successful commissioning D + 18 Months | 36 months required for execution | Contractual | Kindly refer to Amendment 01.
119 |  | 301/354 | Annex-B | The substrata comprising of gravel and boulders is non-conducive to pile boring. Drilling of pile bore may be possible with DTH. However, there is significant issue of bore collapse necessitating the use of casing. On account of colder climate, the sub-strata shall also be prone to permafrost. | MMS pile concreting Is extremely challenging due to the unstable subsurface and the hole collapses after drilling due to freeze-thawing and temperature control of concrete is also very difficult. Moreover the severe weather conditions often shorten the construction season. By considering the difficulty at site, contract period may please be increased to 36 months. | Contractual | Kindly refer to Amendment 01.
120 |  | 301/354 |  | The possibility of encountering weakened bridges that may limit the quantum of transport, in addition to the consideration of navigating through sharp turns and narrow valleys in their logistics strategy as regards to vehicle type and weight transported, shall also be considered by the EPC contractor | The steep terrain and rugged conditions existing in permafrost regions also limit access options (site might not approachable during winter) and approach to site is not motorable for movement of heavy loaded vehicles. Hence road blockage due to heavy snowfall to be considered as Force Majeure. | Projects | The terms and conditions of the tender document shall prevail.
121 |  |  |  | Concrete works for Fening piles | When sm­aller amounts of concrete or grout are involved, such as micro piles, sub-zero ground te­mpera­tures can cause it to freeze before at­ta­ining the appropriate bearing capacity. The concrete will be severely weakened if it freezes before it can reach its full strength, which limits the applicability of concrete structures in these regions. Hence alternative fencing proposal by bidder to be accepted during detail engineering. | Civil - technical | Bidder's execution schedule shall ensure that concreting is done during favourable temperature conditions. Accordingly, the terms and conditions of the tender document shall prevail..
122 |  | 165/354 | 16.2.3 | Contractor shall provide storage cabin having area adequate for storage of plant spares including PV Modules, cables, MMS spares, etc. Storage cabin shall be of PEB (Pre-engineered building) type with RCC framed structure up to plinth level with foundations, columns, beams and RCC grade slab. | PV modules & MMS structures to be allowed for open storage as per OEM recommendation without shed as per Sub section-D | Civil - technical | The terms and conditions of the tender document shall prevail.
123 |  | 165/354 | 16.2.1 | MCR building may be provided with mono/dual slope gable roof system with adequate slope (Min 10 deg) and the ridge line aligned with the predominant wind direction to minimize snow accumulation. | Concrete sloped roof is time taking & tedious construction at this extreme weather By considering the difficulty at site, contract period may please be increased to 36 months. | Projects | Kindly refer to Amendment 01.
124 |  | 185/354 | 37.9 | Switch yard control building and other buildings shall be provided as required as per approved building layout. The buildings shall be of RCC framed structure. | RCC construction at this extreme weather By considering the difficulty at site, contract period may please be increased to 36 months. | Projects | Kindly refer to Amendment 01.
125 |  | 186/354 | 39.3 | BESS container shall be supported on RCC framed structure with plinth and shallow | RCC construction at this extreme weather By considering the difficulty at site, contract period may please be increased to 36 months. | Projects | Kindly refer to Amendment 01.
126 |  |  | 16.2.1 | MCR Building shall be RCC framed Structure. | PEB building may be allowed by considering the extreme weather condition. | Civil - technical | The terms and conditions of the tender document shall prevail.
127 |  |  | 36 | Underground tank RCC Structures for PV Module Cleaning System | Not possible to construct at sub-zero condition. Water freezing will collapse the tank by increase in volume. Insulated water over ground water tank to be allowed. | Civil - technical | Accepted
128 |  | 172/354 | 25.2 | In MCR building, the supervisor room, Conference room and SCADA room shall have Hot and Cold type air conditioning units. | Kindly allow for Heating system as a separate unit, not a part of air conditioning units. | Civil - technical | Heating system may be a separate unit. Kindly refer to Amendment 01.
129 |  |  | General | Module washing system & water supply pipes | Water pipes burst in winter because water expands as it freezes, which causes pressure to build up in the pipes and can lead to them bursting. Kindly allow to provide only dry cleaning system. | Civil - technical | Contractor may propose Wet or Dry type Module Cleaning System. Kindly refer to Amendment 01.
130 |  | 323/354 | 10.3 | Ground Snow Load, So = 2.05 kN/m2. | Kindly allow us to design as per IMD data and IS 875 (Part-4) | Civil - technical | The given value of Ground Snow Load is based on IS 875- Part 4. Hence, terms and conditions of the tender shall prevail.
131 |  | 25/354 | 6.3 | Road : Topping: Either 2 course surface bituminous dressing conforming to Cl. 505 of MORD specs or 20 mm thick open graded pre-mix carpet + Type – B or Type –C seal coat conforming to Cl. 506 of MORD specs. shall be provided. | Bituminous paved surfaces are not an op­tion for this terrain configuration, as bituminous works require ambient temperatures of a minimum of 16 °C and laying temperatures ran­ging from 120 °C to 150 °C. Achieving the­se temperatures in perma­fro­st regions is very difficult. Kindly allow to lay road with subbase and base course without topping. | Civil - technical | Bidder's execution schedule shall ensure that laying of bituminous topping is done during favourable temperature conditions. Accordingly, terms and conditions of tender shall prevail.
132 | Sub-Section A: SOW | 6/354 | General | Revenue land (Owned by Ladakh Autonomous Hill Development Council (LAHDC)) | Any charges to be paid to LAHDC annually? | Contractual | Payment of charges to LAHDC is not in the Scope of the Contractor
133 | A: SOW | 7/354 | Project Particulars | ABT Meter at the 66 kV Plant End Substation | ABT meter will be in the POC to 66kV Phyang S/s line ? Or at plant end 66kV switchyards | Electrical - Technical | At the plant end Sub-Station. Please refer Clause 1 Project Particulars of the Scope of Works.
134 | A: SOW | 7/355 | Project Particulars | Note: PR shall be estimated as per the procedure mentioned in General Annexure-J: FG Test Procedure. - 87% for Operational acceptance | wrt Leh snowfall profile and Rain profile - only 3to 4 months - Radiation to module will be good. Dry cleaning to be used for module washing / Cleaning . PR may not be 87% at all the months. so SECI may allow vendor to start O&M When plant is declared functionally OK. Operational acceptance test may be allowed to conduct during O&M. | Electrical - Technical | Please refer S. No. 9 of Amendment for Module Cleaning . Please refer S. No. 2 of Amendments for PR.
135 | A: SOW | 7/356 | Project Particulars | During O&M period Minimum Guaranteed Generation - CUF - 36.1% | wrt Leh snowfall profile and Rain profile - only 3to 4 months - Radiation to module will be good. BESS Aux Power consumption will also be high . Considering above - minimum guaranteed generation CUF may be provided. | Electrical - Technical | Minimum Guaranteed Generation may be read as Minimum Guaranteed CUF. Please refer S. No. 4 of Amendment.
136 | A: SOW | 7/357 | Project Particulars | Detailed site EHS plan, fire safety & evacuation plan and disaster management plan. | Details of Previous cloud burst and other disaster may be provided to plan accordingly. | Projects | Relevant details are available in public domain. Bidders are requested to refer the same.
137 | A: SOW | 8/357 | 3.2 | The contractor shall estimate the Plant Generation/Energy Yield based on Solar Radiation and other climatic conditions prevailing at site using industry standard simulation software. Simulation report shall be submitted along with the design basis report. | Details of GHI and GTI per month , AC grid limitation Power , Uc , Uv values may be provided by SECI for PVsyst simulation and it will be common to all bidders for calculation. | Electrical - Technical | These parameters shall be as per the design of the contractor. Reference GHI has ben provided to calculate Radiation Correction Factor for CUF calculation.
138 | A: SOW | 9/357 | 3.4 | Transmission line drawings and erection plans as per Electricity Department/DISCOM / STU / CTU guidelines | SECI may provide basic SLD with Solar PV , PCU , IDT , BESS Battery , PCS , PCS Transformer , ABT Metering , TEM metering , 11kV , 66kV Bays with equipment's , POC , Existing 66kV Transmission line details. | Electrical - Technical | Design shall be in the Scope of the Contractor with due consideration to Metering, Point of Interconnection, equipment ratings, Leh PDD requirements etc. as provided in the Specifications.
139 | A: SOW | 12/354 | 4.15 | Design & Construction of 66 kV LILO Over Head Transmission Line including Towers, Conductors, OPGW cable, Insulators, Cable Termination Kits and associated accessories from Plant end Substation to the interconnection point as per CTU/Leh PDD drawings/specifications including Right of Way, permits and approvals, CTU/Leh PDD supervision and maintenance charges. | SECI may provide the Basic planned route for 66kV line (ROW) , tower to tower distance. | Electrical - Technical | Tower Nos. have been mentioned. Distance from these tower shall depend on the location of 66/11 kV Sub-Station, which is in the scope of the contractor.
140 | A: SOW | 16/354 | 8.3 | All royalties and taxes as required to be paid for excavation of earth / rocks / sand shall be borne by the Contractor | SECI may further explain wrt Royalties | Projects | The terms and conditions of the tender document shall prevail.
141 | A: SOW |  | 10.3 | To provide a detailed training plan for all O&M procedures to Employer’s nominated staff, which shall have prior approval from the Employer. | Training will be provided only at site , all travel , Stay and other charges need to be borne by SECI | Electrical - Technical | Accepted.
142 | B: TS-Electrical |  | 2.3 | Warranty The SCB unit shall be warranted against all material/ manufacturing defects and workmanship for minimum of 2 (two) years from the date of supply. | Usually SCB will be supplied with one year warranty , same may be accepted. | Electrical - Technical | The terms and conditions of the tender document shall prevail.
143 | B: TS-Electrical | 30/354 | 4.2.1 | The Inverter Supplier shall be Class-I local supplier | Class I supplier may be relaxed . Many PCU /PCS vendors may not be confirming for stable PCU/PCS working at 3.5KMS altitude. | Electrical - Technical | This is in line with the Public Procurement (Preference to Make in India) Order 2017. Terms & Conditions of Tender shall prevail.
144 | B: TS-Electrical | 57/354 | 11.2.1 | 110 V / 220 V DC system (Battery, Battery Charger & DCDB) in accordance with this specification and standards stated herein, shall comprise of the following. (i) Sealed Maintenance Free VRLA battery complete with racks & accessories. | SECI may allow UPS + NI CD Battery - for Project - since it includes 10 years O&M. (VRLA batteries will last for 3 years averagely) | Electrical - Technical | The terms and conditions of the tender document shall prevail.
145 | B: TS-Electrical | 61/354 | 12.3.1 | All PV Modules, Module Mounting Structures (MMS) and String Combiner Box (SCB) structures in the PV array field shall be bonded to the earthing system by two distinct connections. | EPC understanding is module to module earthing not required - since all modules are connected to MMS . | Electrical - Technical | The terms and conditions of the tender document shall prevail.
146 | B: TS-Electrical | 68/354 | 15.5.8 | Data Communication to SLDC/RLDC: SCADA system shall provide required interface to integrate with SLDC/RLDC, in compliance with grid code, to send any parameters specified by SLDC/RLDC. | Any Extra Hardware device required at Leh SS /Phyang SS /PGCIL SS for Data communication? Same shall be intimated by SECI. | Electrical - Technical | The terms and conditions of the tender document shall prevail.
147 | B: TS-Electrical | 109/354 | 2.1 | 11 kV / 415 V, 50 Hz, 3 phase The BESS will be coupled with the PV System at the AC Bus on the MV (11 kV) side of the Inverter Transformers. | SECI may provide Basic SLD with Solar PV , PCU , IDT , BESS Battery , PCS , PCS Transformer , ABT Metering , TEM metering , 11kV & 66kV Bays with equipment's , POC , Existing 66kV Transmission line details. | Electrical - Technical | Design shall be in the Scope of the Contractor with due consideration to Metering, Point of Interconnection, equipment ratings, Leh PDD requirements etc. as provided in the Specifications.
148 | B: TS-Electrical | 119/354 | 4.11.2 | The auxiliary supply to the BESS shall be metered separately. Meters shall be TVM of 0.2 accuracy. | EPC vendor need to Pay any extra charges for the BESS auxiliary owner drawn from Grid? | Electrical - Technical | The Contractor shall guarantee minimum CUF based on Net Energy Exported from the Plant as per the O&M Agreement (Section VII , Sub Section F of the TS).
149 | B: TS-Electrical | 122/354 | 5.15 | The DAS shall be capable of making all monitored data and events available through the DNP3 / IEC 61850 communication interface and shall permit display of current values and recent historical trends on a local screen for all recorded points | Usually PCS are not DNP3 compactable, DAS with modbus TCP/IP may be accepted. | Electrical - Technical | The terms and conditions of the tender document shall prevail.
150 | B: TS | 137/354 | 2.1 | 2.1 The contractor shall be responsible for detailed Topographical Survey of the proposed project site. The work shall be carried out through an agency with relevant experience and qualified survey team. 2.2 The Topographical survey shall be conducted at 20m x 20m grid, or as directed by the Employer, only with the help of digital surveying instruments like Total Station/ Auto level. | SECI may provide any previous topo survey and piling Pull out test details . | Electrical - Technical | Topography Survey and Geotechnical Investigation is in the Scope of the Contractor. However, Topography survey Report and Geotechnical Survey Report based on past surveys have been provided in the Specific Annexures D and C respectively for reference purpose only. Please refer Sl.No. 23 and 25.
151 | B: TS |  | 16.2.1 | MCR | Any heater is envisaged in MCR ? | Electrical - Technical | As per Clause 25.3 of Subsection C of Section VII, heating systems to maintain temperature suitable for performance of equipment and comfort of occupants shall be provided.
152 | Plant Documentation, Commissioning & Test Procedure | 289/354 | 6.6 | Criterion: ηp, as determined through the process described above shall be at least equal to the guaranteed RtE described elsewhere in this document at the time of commissioning | Performance test of BESS - RtE values as per site test need to match the RtE described. | Electrical - Technical | Yes
153 |  | 292/354 | 2 | FUNCTIONAL GUARANTEE TESTS FOR SOLAR PV PLANT Cumulative Plant Generation measured at Plant End ABT meter over the duration of reporting period (kWh), (1/4) hour | Solar 11KV feeder is taken as reference for Solar PV plant PG test ? | Electrical - Technical | Yes. Plant Performance Ratio Test be measured at the 11 kV HT Voltage Bus. Please refer Amendment-1 (S.No.5)
154 | SUB-SECTION D GENERAL ANNEXURE J Functional Guarantee (FG) Test Procedure | 294/354 | 2.1.4.2 (2) | Grid Interruptions – Time periods (15-minute time blocks) of the grid interruptions at the utility substation, recorded manually jointly by EPC Contractor and SECI representatives shall be eliminated. Grid outage period, if any, shall be verified from SCAD | Grid outage time need to include with plant restoration time . Total Grid outage time = Grid outage duration + plant restoration duration. | Electrical - Technical | Please refer S. No. 11 of Amendment
155 |  | General |  | BESS discharge | Whether any Scheduling for BESS discharge is envisaged? | Electrical - Technical | BESS shall be scheduled to discharge in the non-solar hours.
156 |  | LD |  | LD during PG test and O&M | Maximum cap may be fixed for LD during PG test and O&M | Electrical - Technical | Please refer Clause 3 - Liquidated Damages for Shortfall in PR in the SUB-SECTION D General Annexure J: Functional Guarantee (FG) Test Procedure and For LD during O&M, please refer Annexure 2 to SUB-SECTION F OPERATION & MAINTENANCE AGREEMENT.
157 |  | PPA |  | PPA | SECI PPA rate may be mentioned. | Electrical - Technical | NA
158 |  | O&M |  | Guaranteed CUF during First Year is 36.1% | SECI may provide each months GHI since O&M billing is for four months once. | Electrical - Technical | As per the terms of the O&M Agreement, CUF shall be calculated on annual basis. Liquidated damages, if any, on account of shortfall in CUF shall be adjusted from final Bill.
159 |  | General |  | During Site visit it is understood that - PGCIL Leh , Pyangong Each phase transformer (16.67MVA -) is carried separately | SECI may provide - Maximum Tonnage can be carried in Leh roads connected to Kargil , srinagar. | Electrical - Technical | Contractor shall carry out logistics survey to determine maximum tonnage, as required.
160 |  | General |  | O&M | During O&M - Equipment failure - If no spares is available , transportation is not possible. Then SECI may declare the same under force majeure. | Electrical - Technical | The terms and conditions of the tender document shall prevail.
161 | TS Technical | 112/354 | 3.1.1 | The BESS Supplier/Sub-Contractor must have experience of having successfully completed ‘Design, Engineering, Procurement, Construction, Installation, Testing and Commissioning of Grid Connected Battery Energy Storage System (BESS)’ of at least 02 (Two) Grid connected BESS Plants, each having an individual capacity of 2 MWh (Five Mega Watt Hour) or above in last five years. However, such BESS Plant capacity must have been in satisfactory operation for at least 12 (Twelve) months from the date of commissioning. | Whether experience of two projects of 2 MWh each or Five MWh each required. Please clarify. | Electrical - Technical | Experience of two projects of 2 MWh each. Please refer Amendment-1 (S.No.7)
162 | SECI/C&P/OP/11/014/2024-25 | 94 of 114 | 3.4.1 | Note: For the purpose of system nameplate sizing subject to the minimum specified in Table 2: Supply-Specific Ratings and Requirements above, the Contractor shall consider 4 hours of discharge during the post-solar hours | As per Power rating is 20MW, the discharge capacity is 10MWh for 4 hours or rated power 20MWh for 4 hours | Electrical - Technical | Required Dispatchable BESS capacity is 40 MWh with maximum dispatch of 20 MW at POC. However, as per this clause, 4 hours of discharge @ 10MW shall be considered for design and sizing calculations during detailed engineering.
163 | SECI/C&P/OP/11/014/2024-25 | 101 of 114 | 4.11 | The BESS shall include an auxiliary power system (separate or same as the Solar Plant auxiliary system). comprising of step-down transformers, breakers, fuses, relaying, panels, enclosures, junction boxes, conduits, raceways, wiring, etc., as required for the BESS operation | Aux.Supply shall be considered extra Aux.Transformer in day time during solar generation and night shall be from grid | Electrical - Technical | BESS shall be sized so as to meet the auxiliary Power requirement for BESS during night. It may be noted that the CUF guarantee is based on net energy exported.
164 | General |  |  | Tentative Cable distance for 66kV line |  | Electrical - Technical | Tower Nos. have been mentioned. Distance from these tower shall depend on the location of 66/11 kV Sub-Station, which is in the scope of the contractor.
165 | SECI/C&P/OP/11/014/2024-25 | 102 of 114 | Sub-section B 5.7 | Event logging / Digital data | Duration not mentioned – please specify. | Electrical - Technical | Event log for 6 months period shall be maintained. Please refer S. No. 20 of Amendment.
166 | SECI/C&P/OP/11/014/2024-25 | 93 of 114 | Sub-section B 3.1 table 2 | Grid Charging – No | Is there a future plan to connect grid? | Electrical - Technical | The subject PV Plant is grid connected. There is no future plan of Grid charging of BESS. BESS shall be charged from Solar Generation only.
167 | SECI/C&P/OP/11/014/2024-25 | 94 of 114 | Sub-section B 3.4.1 | Peak management (PM) | As per our understanding use case is PV utilization rather than peak management. Please confirm. | Electrical - Technical | It is Peak Management only. Specifically, storage of a fraction of energy generated during the solar hours, and dispatch of the same during non solar hours.
168 |  |  | Section C - EMS 3.1 | EMS functionality for the Plant Control | Please clarify the control hierarchy of EMS and Solar SCADA. | Electrical - Technical | Functions and Controls defined in the EMS shall hold priority over Solar SCADA so as to meet the technical standards of connectivity requirement.
169 |  | 47 of 114 | Sub-section B 15.2.5 | Data storage for 2 years required | All plant data should be on local server only or can we propose a cloud-based storage alternative? | Electrical - Technical | Plant data shall be stored in local as well as virtual/Cloud server. Please refer Clause 15.2 of the Technical Specification along with S. No. 22 of Amendment.
170 |  |  |  |  | Please clarify the short-term and long-term data archival intervals | Electrical - Technical | Query Not Clear.
171 | SECI/C&P/OP/11/014/2024-25 | 3 of 15 | 1 Project Particulars | BESS Power Rating-Nameplate rating: 50 MWh with minimum 40 MWh Dispatchable capacity at the Beginning of Life | Nameplate rating: 50 MWh DC with minimum 40 MWh AC Dispatchable capacity at the Beginning of Life | Electrical - Technical | Query Not Clear.
172 |  | 3 of 15 | 1 Project Particulars | Origin of Supply Items-As per MNRE Order on Public Procurement (Preference to Make in India) to provide for Purchase Preference (linked with local content) in respect of RE Sector dated 9th February, 2021 and subsequent amendments | linked with local content can be modified or delete | Electrical - Technical | The terms and conditions of the tender document shall prevail.
173 |  | 3 of 15 | 1 Project Particulars | Point of Interconnection -66 kV Loop-in-Loop-out (LILO) in 66 kV I/C line from Phyang S/s to 66 kV O/G line to Leh S/s Tower No: From 326 to 325 | Cable size and cable distance to be required | Electrical - Technical | Tower Nos. have been mentioned. Distance from these tower shall depend on the location of 66/11 kV Sub-Station, which is in the scope of the contractor. Please refer updated Specific Annexure SA-A: Tentative Land Layout for Tower locations. Please refer S. No. 24 of Amendment 1.
174 | Sub-Section B: TS-Electrical | 92 of 114 | 2.1 | Electrical infrastructure: AC system interconnection requirement at Point of Common Coupling (PCC) - 11 kV / 415 V, 50 Hz, 3 phase The BESS will be coupled with the PV System at the AC Bus on the MV (11 kV) side of the Inverter Transformers | 66kV/11kV Transformer is in BESS supplier scope of it will be free issue | Electrical - Technical | Query Not Clear
175 | Sub-Section B: TS-Electrical | 93 of 114 | 3.1 | Energy rating*, (B)-Minimum 50 MWh Nameplate capacity with at least 40 MWh dispatchable at the beginning of life and not less than 80% of this capacity i.e. 32 MWh at any point of time up to End of Battery Life | 80% of this capacity i.e. 32 MWh at any point of time up to End of Battery Life on Which year need to consider at 80% | Electrical - Technical | End of Life: Please refer Cl. 4.4 (TS-Electrical-B(BESS) for Design Life of BESS.
176 |  | 93 of 114 | 3.1.1 | The BESS Supplier/Sub-Contractor must have experience of having successfully completed ‘Design, Engineering, Procurement, Construction, Installation, Testing and Commissioning of Grid Connected Battery Energy Storage System (BESS)’ of at least 02 (Two) Grid connected BESS Plants, each having an individual capacity of 2 MWh (Five Mega Watt Hour) or above in last five years. However, such BESS Plant capacity must have been in satisfactory operation for at least 12 (Twelve) months from the date of commissioning | Need to modification for 1MWh | Electrical - Technical | The terms and conditions of the tender document shall prevail.
177 | SECI000153-93181-TechnicalTenderDocument |  |  |  | Please share approved Vendor list | Electrical - Technical | No approved Vendor list has been specified. EPC Contractor shall submit equipment GTP meeting technical specifications as per tender to the Employer during detailed engineering.
178 | SECI000153-93181-TechnicalTenderDocument |  |  |  | Fault level at 11 kv Require. | Technical | System Fault current has been mentioned in Cl. 6 (TS-Electrical)
179 | SECI000153-93181-TechnicalTenderDocument |  |  |  | AutoCAD/ KMZ file require | Technical | Please refer Specific Annexure: A, site layout along with coordinates have been provided.
180 | SECI000153-93181-TechnicalTenderDocument |  |  |  | Termination SLD require | Technical | SLD is in the Scope of the Contractor. Please refer Scope of Works for Interconnection details.
181 |  |  |  |  | Indicative SCADA Schematic Diagram & I/O List require | Technical | Please Refer General Annexure GA-H: SCADA Schematics and I/O List (Indicative) - S. No. 21 of Amendment 1.
182 | SECI000153-93181-TechnicalTenderDocument,Sub Section-C | 144 | 6.9 | Roads | Bidder is requesting to confirm 2.5m wide well compacted corridor should be filled with Murrum | Technical | The terms and conditions of the tender document shall prevail.
183 | SECI000153-93181-TechnicalTenderDocument,Sub Section-C | 177 | 35 | PV Module Cleaning System | Bidder understood that Module Cleaning System as Wet Cleaning System. Kindly confirm. | Technical | Bidder may propose Wet or Dry type Cleaning System as per clause No.35 under Subsection-C of Section-VII . Please refer Sl. No. 9 of Amendment 1.
184 | SECI000153-93181-TechnicalTenderDocument,Sub Section-C | 144 | 5.4 | Area Grading and Land Development | a) Bidder understood that Tree's cutting is in EPC Scope. b) Please provide Top survey report for the Project, if available. | Technical | a) Yes b) Topographical Survey shall be in the scope of the bidder. However, a topographical survey Report based on past survey is provided for reference purposes only. Please refer S. No. 26 of Amendment 1.
185 | SECI000153-8133286-ContractualTenderDocument | 159 | GCC-24 | Contract Performance Security | CPBG Expiry is kept till 10 years which is unusually high duration with respect to industry standards, we Request SECI to separate CPBG- valid till completion of DLP period and O&M BG-5% of O&M value valid till Completion of O&M. | Contractual | The terms and conditions of the tender document shall prevail.
186 | SECI000153-8133286-ContractualTenderDocument | 161 | GCC_80.1 | Schedule of Rates & Payments | for a better cash flow during O&M period, we Request client to Remove the 10% BG post completion of BG Test, as O&M Bank Guarantee is a better substitute to it. | Contractual | The terms and conditions of the tender document shall prevail.
187 |  |  | Annexure to BDS |  | We, Enerture Technologies Pvt Ltd is a well-established EPC, IPP developer player in the Renewable Energy Segment since 2012. We are very serious player and are meeting all the Technical Parameters of the above mentioned tender and would be bidding for the above tender. We request you to consider Provisional Balance FY 23-24 Turnover figures duly certified by our CA along with Audited Balance Sheet for the FY 22-23, 21-22 for meeting Min Avg Annual Turnover (MAAT) criteria. | Contractual | The terms and conditions of the tender document shall prevail.
188 | 1. General Requirement | Pg 4 of 57 | 1.4.5 | General Requirement- As per project requirements, the Employer may ask for approval of all civil designs and drawings by IITs/NITs, the cost of which is included in the bid price. | Request SECI to allow bidder approved designs which can be discussed and finally approved during detailed engineering with SECI. | Technical | The terms and conditions of the tender document shall prevail.
189 | 4. Other Investigations | Pg 11 of 57 | 1.5 | The area at and around (up to 10m beyond external wall/ area including access road & parking whichever is minimum) all buildings/ plinth for open installations (MCR, ICR, etc.), transformer yard and switchyard shall be uniformly levelled at suitable RL (i.e. FGL) to be finalized considering topography and HFL at site. | Request SECI to consider that levelling the said ground up to 10m (MCR, ICR & open installation etc..) is not required. | Technical | The terms and conditions of the tender document shall prevail.
190 | 5 Area Grading and Land Development | Pg 12 of 57 | 5.4 | The slope at edge of graded areas shall not be steeper than 1:1.5 (1 Vertical: 1.5 Horizontal) in cutting and 1:2 (1 Vertical: 2 Horizontal) in filling with provisions of slope protection (as necessary). | a) Request SECI to remove the requirement for Slope protection (Stone pitching). b) Tentative Land Layout is not available in Special Annexure SA-A. c) Since the proposed land layout/location/co-ordinate (299/354) is the same as old location, request SECI to provide topo & Geotech. | Technical | a) Requirement for slope protection shall prevail as per tender. b) Please refer S. No. 24 of Amendment 1. c) Topographical Survey and Geotechnical Investigation shall be in the scope of the bidder. However, Geotechnical Investigation Report including bore log, trial pit log, soil test results and ERT results is attached as Specific Annexure - SA-C: Geotechnical Investigation Report for reference and general information of the bidder only.
191 | 7. Civil Works | Pg 12 of 15 | 7.15 | Approach road to the Project site has been identified in Sub Section E (Specific Annexures: SA-A: Tentative Land Layout). The scope of works for Approach Road shall include re-compaction/re-rolling, filling of WBM (if required), provision of culvert and drain and bituminous topping as per detailed specifications. | Approach road along with tentative Land Layout is not available in Special Annexure SA-A. | Technical | Refer page 299 of 354 of Section VII. Please refer Annexure to Amendment 1 wherein amended Sub Section - E has been provided.
192 | 4. Other Investigations | Pg 11 of 57 | 4.3 | Target mean strength of concrete for mix design shall be based on σ (standard deviation) = 5. | Request SECI to allow us to consider standard deviation as per IS456 code recommendation. | Technical | The terms and conditions of the tender document shall prevail.
193 | 6. Roads | Pg 14 of 57 | 6.9 | 2.5m wide well compacted corridor shall be left along inside of the plant boundary suitably maintained clean of any vegetation and shall be provided with adequate illumination for movement of security personnel. Any undulations shall be made good with locally available coarse grained material to have fairly level passage way. | Requesting SECI to avoid the peripheral road levelling. Can we do only compaction on the existing ground profile? | Technical | The terms and conditions of the tender document shall prevail.
194 | 7. Surface/ Area drainage | Pg 15 of 57 | 7.11 | For areas of grading, toe drain shall be provided along the bottom of the slope. | Requesting SECI to avoid the toe drain. | Technical | The terms and conditions of the tender document shall prevail.
195 | 7. Surface/ Area drainage | Pg 16 of 57 | 7.16 | The drain outfall shall be connected to the nearest existing natural drain(s)/ water body outside plant premises and it shall be ensured that the drainage water shall not re-enter the plant nor encroach/ flood in the adjacent property/ plot. | If the nearest existing rain/water body is not available, instead of connecting the existing drain can we propose the more no of recharge pit and ground level culvert where ever required. | Technical | Kindly refer Amendment 01.
196 | 14 Concrete Works, 33 Pipe & Cable Trenches | Pg 31 and 43 of 57 | 14.7, 33.4 | 14.7 MS Angles of minimum size 50 x 50 x 6 mm with 8 mm dia - 150mm long MS lugs @ 150mm c / c shall be provided for edge protection around all cutouts / openings in RCC floor slabs / walls, edges of drains supporting grating / pre-cast covers, edges of manhole supporting covers, around periphery of all removable pre-cast covers and any other place where breakage of corners of concrete is expected. 33.4 Min. thickness of precast cover shall be 50mm. Both bearing edges of the cable trench and all edges of pre-cast concrete covers shall be provided with min. 50x50x6 mm edge protection angle with MS lugs. | Requesting SECI to avoid the edge angles on precast concrete covers. | Technical | The terms and conditions of the tender document shall prevail.
197 | 16 Buildings and Plinth (Support Structure) for Open Installations | Pg 32 of 57 | 16.1.2 | 16.1.2 Unless otherwise specified elsewhere, all buildings and plinth (support structure) for open installations except Security room/ cabin shall have RCC framed structure. Masonry partition walls shall be provided for Kitchen, Pantry, Battery room and Toilet units. For other rooms, AL Glass partitions shall be provided. The size of the plinth (framed structure) for open installations and equipment area shall as per OEM requirements. | Can we avoid the RCC framed structure for open installation or It can be modified as per design requirement or it can be finalized at the time of detail engineering based on input requirement. | Technical | The terms and conditions of the tender document shall prevail.
198 | 17 Buildings and Plinth (Support Structure) for Open Installations | Pg 34 of 57 | 16.2.3 | 16.2.3 Storage cabin for plant Spares • Contractor shall provide storage cabin having area adequate for storage of plant spares including PV Modules, cables, MMS spares, etc. | Area of the storage cabin is not mentioned. Can we use the container as a storage cabin? | Technical | The terms and conditions of the tender document shall prevail.
199 | 39 BESS Yard Civil Works | Pg 54 of 57 | 39.3 | 39.3 BESS container shall be supported on RCC framed structure with plinth and shallow foundations. Support structure shall be in line with the OEM requirements. | Can we avoid the RCC framed structure for BESS Container or It can be modified as per design requirement or it can be finalized at the time of detail engineering based on input requirement. | Technical | Kindly refer Amendment 01.
200 | 78 (ii) Routine Tests Pull out and Lateral | Pg 3 of 21 | 78 (ii) | 1. The piles for routine tests shall be selected at Random to represent total no. of job piles. 2. The pile test shall be carried out as per approved methodology. | 1. As the pile depths are proposed based on pile test report/Geotech report, requesting to SECI to avoid the Routine test. 2. Requesting the SECI to eliminate the, holding of 2.5 times working load on the test pile for 24 hrs. | Technical | 1. The terms and conditions of the tender document shall prevail. 2. Modification in loading duration can be done subject to SECI's approval during detailed engineering.
201 | 4.6 Battery Subsystem Design Requirements |  | General |  | Requesting SECI to mention about the ancillary functionalities required by BESS or not. | Technical | The use case specified for BESS is Peak Management (Energy Shifting). Ancillary services functionalities are not envisaged under the specifications.
202 |  |  | General |  | Requesting SECI to confirm if above ground cable laying will be a option to bidder. | Technical | As per terms and conditions specified in the tender document.

## Amendment-1
Tender No : SECI/C&P/OP/11/014/2024-25
Tender for Design, Engineering, Supply, Construction, Erection, Testing, Commissioning and O&M of 25 MW (AC) Solar PV Power Plant (50 MWp DC) with 20 MW / 50 MWh Battery Energy Storage System at Taru, Leh, UT of Ladakh, India
S. No. | Section | Sub-Section | Page No. | Clause | Original Version | Amendment
1 | SECTION V Special Conditions of Contract | Definitions | 2 of 10 | 3 | The Time for Commissioning for the project along with other associated equipment as per this tender document in total shall be 18 (Eighteen) Months from the Date of signing of Contract Agreement. | The Time for Commissioning for the project along with other associated equipment as per this tender document in total shall be 36 (Thirty Six) Months from the Date of signing of Contract Agreement.
2 | SECTION V Special Conditions of Contract | SCC 3 | 2 of 10 | 3
3 | Annexure to BDS | Financial Eligibility Conditions | 6 of 11 | 1.3 | The bidder should have a minimum Working Capital of INR 62,00,00,000/- (Indian Rupees Sixty-Two crores only) as per the last audited financial statement. If the bidder’s working capital is inadequate, the bidder should supplement this with a letter from the bidder’s bank, having net worth not less than INR 500 Crores, confirming availability of the line of credit for more than or equal to INR 62,00,00,000/- (Indian Rupees Sixty-Two crores only) to meet the working Capital requirement of this particular Project. | The bidder should have a minimum Working Capital of INR 31,00,00,000/- (Indian Rupees Thirty One crores only) as per the last audited financial statement. If the bidder’s working capital is inadequate, the bidder should supplement this with a letter from the bidder’s bank, having net worth not less than INR 500 Crores, confirming availability of the line of credit for more than or equal to INR 31,00,00,000/- (Indian Rupees Thirty One crores only) to meet the working Capital requirement of this particular Project.
4 | SECTION V Special Conditions of Contract | Contract Performance Security (GCC clause 24) | 5 of 10 | 9 | Against EPC/ LSTK & O&M Contract of the project, within 30 (Thirty) days from the issuance of the Notification of Award/ Letter of Intent/Letter of Award, the successful bidder shall furnish unconditional and irrevocable individual Bank Guarantees issued by any Nationalized Banks in the manner as mentioned below. The Contract Performance Security shall be in the form of Bank Guarantee only and shall be in the currency of the Contract and will be issued in the name of the Owner as “Solar Energy Corporation of India Ltd”. The Contract Performance Security against this Contract need to be furnished as mentioned below: 1. First Stage (Supply and Services): The value of the Contract Performance Security shall be 5% (Five percent) of the Contract Value (i.e., total sum of the Supply & Service Contract). This Performance security will be valid for a total period of 141 Months (18 Months Project commissioning period) + prescribed O & M Period, i.e., 120 Months + 03 Months additional) from the date of its issuance. The successful bidder can submit Contract Performance Security with initial validity of 36 months and the same may be extended after every 36 months till completion of the total 75 months period. | Against EPC/ LSTK & O&M Contract of the project, within 30 (Thirty) days from the issuance of the Notification of Award/ Letter of Intent/Letter of Award, the successful bidder shall furnish unconditional and irrevocable individual Bank Guarantees issued by any Nationalized Banks in the manner as mentioned below. The Contract Performance Security shall be in the form of Bank Guarantee only and shall be in the currency of the Contract and will be issued in the name of the Owner as “Solar Energy Corporation of India Ltd”. The Contract Performance Security against this Contract need to be furnished as mentioned below: 1. First Stage (Supply and Services): The value of the Contract Performance Security shall be 5% (Five percent) of the Contract Value (i.e., total sum of the Supply & Service Contract). This Performance security will be valid for a total period of 159 Months (36 Months Project commissioning period) + prescribed O & M Period, i.e., 120 Months + 03 Months additional) from the date of its issuance. The successful bidder can submit Contract Performance Security with initial validity of 36 months and the same may be extended after every 36 months till completion of the total 159 months period.
5 | SECTION - VII SUB-SECTION B | Part B: Battery Energy Storage System | 93 of 114 | 3.1 | BESS Availability: 98% | BESS Availability: 95%
6 | SECTION - VII SUB-SECTION A | TS-Scope of Works | 4 of 15 | 1 | Performance Ratio (at 11 kV HT Voltage Bus): 87% | Performance Ratio (calculated as per General Annexure F : FG Test Procedure): Jan 81.1% Feb. 84.5% March. 79.6% April. 77.8% May. 81.8% June. 79.7% July. 82.8% August 75.9% September. 79.0% October. 80.0% November. 78.4% December. 78.8% Note: In case of PR Test being conducted across different months, the guaranteed PR shall be calculated as the weighted average of PR for the month (as per above table) and the no. of days in the month over which PR test is conducted.
7 | SECTION - VII SUB-SECTION D | GENERAL ANNEXURE J Functional Guarantee (FG) Test Procedure | 4 of 9 | 2.1.2 | Eout: Cumulative Plant Generation measured at Plant End ABT meter over the duration of reporting period (kWh), (1/4) hour Tref : PV Module temperature at which P_o is determined, i.e. 25°C | Eout: Cumulative Plant Generation measured at Solar Feeder Meters at the 11 kV Bus over the duration of reporting period (kWh), (1/4) hour E_(BESS Charge) : Cumulative Plant Generation utilised for BESS charging (measured at BESS Feeder Meters at the 11 kV Bus) over the duration of reporting period (kWh), (1/4) hour Tref: PV Module temperature averaged over the day, weighted by POA, i.e.: Tref = Σ (G_(i,k) * Tavg_mod,k ) / Σ G_(i,k)
8 | SECTION - VII SUB-SECTION A | TS-Scope of Works | 4 of 15 | 1 | Minimum Guaranteed Generation | Minimum Guaranteed CUF
9 | Section - VII | General Annexure-F: FG Test Procedure | 6 of 9 | 2.1.2 | (3) Estimation of Daily PR • For each reporting period (15-min time-block) of cumulative plant generation measured at plant end ABT meter, PR shall be calculated as per the formula given in Clause no. 2.1.2 | (3) Estimation of Daily PR • For each reporting period (15-min time-block), PR shall be calculated as per the formula given in Clause no. 2.1.2
10 | SECTION - VII SUB-SECTION A | TS-Scope of Works | 9 of 15 | 4.12 | 66/11 kV Plant Pooling Substation with required number of 11 kV bays, required no. of 66/11kV transformers, four nos. of 66 kV Bays (Two Transformer Bays, One Line Bay & One Bus Coupler Bay), Bus PTs. Busbars, Equipment of Line Bay and Bus Coupler Bay shall be suitable for evacuation of 25 MW. | 66/11 kV Plant Pooling Substation with required number of 11 kV bays, required no. of 66/11kV transformers, required no. of 66kV bays, Bus PTs. Busbars, Equipment of Line Bay and Bus Coupler Bay shall be suitable for evacuation of 25 MW.
11 | SECTION - VII SUB-SECTION B | Part A: Electrical System | 93 of 114 | 3.1.1 | The BESS Supplier/Sub-Contractor must have experience of having successfully completed ‘Design, Engineering, Procurement, Construction, Installation, Testing and Commissioning of Grid Connected Battery Energy Storage System (BESS)’ of at least 02 (Two) Grid connected BESS Plants, each having an individual capacity of 2 MWh (Five Mega Watt Hour) or above in last five years. However, such BESS Plant capacity must have been in satisfactory operation for at least 12 (Twelve) months from the date of commissioning. | The BESS Supplier/Sub-Contractor must have experience of having successfully completed ‘Design, Engineering, Procurement, Construction, Installation, Testing and Commissioning of Grid Connected Battery Energy Storage System (BESS)’ of at least 02 (Two) Grid connected BESS Plants, each having an individual capacity of 2 MWh (Two Mega Watt Hour) or above in last five years. However, such BESS Plant capacity must have been in satisfactory operation for at least 12 (Twelve) months from the date of commissioning.
12 | SECTION - VII SUB-SECTION B | Part A: Electrical System | 23 of 354 | 1.3 |  | Note: PV Module shall have been tested for design loads applicable at site (Refer TS-Civil, relevant clause on Design Load combinations) with minimum safety factor of 1.5 (as per IEC 61215-2) PV Modules shall conform to MNRE Order on Public Procurement (Preference to Make in India) to provide for Purchase Preference (linked with local content) in respect of RE Sector dated 9th February, 2021 and subsequent amendments.
13 | SECTION - VII SUB-SECTION A | Scope of Works | 12 of 15 | 7.18 | Suitable arrangement of water shall be ensured to cater to day-to-day requirement of drinking water and permanent water supply for module cleaning (in case of wet type Module Cleaning System) and other needs of SPV power plant during entire O&M period. | Construction of wet type or dry type module cleaning system as per specifications. Suitable arrangement of water shall be ensured to cater to day-to-day requirement of drinking water and permanent water supply for module cleaning (in case of wet type Module Cleaning System) and other needs of SPV power plant during entire O&M period.
14 | SECTION - VII SUB-SECTION B | Part A: Electrical System | 102 of 354 | 23 .1 (ii) | (ii) Along the Plant Perimeter: Covering complete perimeter of Plant Area to capture all possible intrusion | (ii) Any strategic location in the Plant Area required to be monitored.
15 | SECTION - VII SUB-SECTION D | GENERAL ANNEXURE J Functional Guarantee (FG) Test Procedure | 294/354 | 2.1.4.2 (2) | Grid Interruptions – Time periods (15-minute time blocks) of the grid interruptions at the utility substation, recorded manually jointly by EPC Contractor and SECI representatives shall be eliminated. Grid outage period, if any, shall be verified from SCADA | Grid Interruptions – Time periods (15-minute time blocks) of the grid interruptions at the utility substation plus time for restoration (subject to a maximum of 30 minutes after grid is available subsequent to an interruption event) , recorded manually jointly by EPC Contractor and SECI representatives shall be eliminated. Grid outage period, if any, shall be verified from SCADA
16 | SECTION - VII SUB-SECTION B | Part A: Electrical System | 70 of 354 | 15.10.2 | Operating System and Database shall be of enterprise scale (RedHat Linux or equivalent Linux OS, Oracle/MySQL or Windows or equivalent DB), with required AMC for 5 years | Operating System and Database shall be of enterprise scale (OS - RedHat Linux or Windows Server or equivalent Linux OS; DB - Oracle/MySQL or Windows or equivalent DB), with required AMC for 5 years
17 | SECTION - VII SUB-SECTION C | TS-Civil, Mechanical and Plumbing Works | 54 of 57 | 39.3 | BESS container shall be supported on RCC framed structure with plinth and shallow foundations. Support structure shall be in line with the OEM requirements. | BESS container shall be supported on RCC framed structure with plinth and shallow foundations. Any other RCC support structure in line with the OEM requirements may also be provided.
18 | SECTION - VII SUB-SECTION C | TS-Civil, Mechanical and Plumbing Works | 172 of 354 | 25.2 | In MCR building, the supervisor room, Conference room and SCADA room shall have Hot and Cold type air conditioning units. | In MCR building, the supervisor room, Conference room and SCADA room shall have Air conditioning units.
19 | SECTION - VII SUB-SECTION C | 7. Surface/ Area drainage | Pg 16 of 57 | 7.16 | The drain outfall shall be connected to the nearest existing natural drain(s)/ water body outside plant premises and it shall be ensured that the drainage water shall not re-enter the plant nor encroach/ flood in the adjacent property/ plot. | The plant drains shall be connected to the nearest existing natural drain(s) inside the plant area which are finally draining the water outside the plant. Such existing natural drains shall be cleaned and developed propel to facilitate effective drainage. The contractor may also propose for recharge pits of adequate size and in adequate numbers to meet the requirement of storm water disposal.
20 | SECTION - VII SUB-SECTION B | Part B: Battery Energy Storage System | Page 93 of 114 | 3.1 | Energy rating*, (B) Minimum 50 MWh Nameplate capacity with at least 40 MWh dispatchable at the beginning of life and not less than 80% of this capacity i.e. 32 MWh at any point of time up to End of Battery Life. | Energy rating*, (B) Minimum 50 MWh Nameplate/Installed capacity with at least 40 MWh dispatchable at the beginning of life (i.e. at the time of Commissioning). Minimum dispatchable capacity at the end of each year of operation shall be as per below table: Year of Operation Dispatchable Capacity Year 1 38.8 MWh Year 2 38.4 MWh Year 3 37.6 MWh Year 4 36.8 MWh Year 5 36.0 MWh Year 6 35.2 MWh Year 7 34.4 MWh Year 8 33.6 MWh Year 9 32.8 MWh Year 10 32 MWh Dispatchable capacity shall not be less than 80% of Beginning of Life capacity at any point of time up to End of Battery Life
21 | SECTION - VII SUB-SECTION D | General Annexure I: Plant Documentation, Commissioning & Test Procedure | Page 18 of 21 | 6.6 | POC | POC may be read as PCC, as defined in Part B: Battery Energy Storage System, 1.2. Definitions
22 | SECTION - VII SUB-SECTION B | Part A: Electrical System | 87 of 354 | 19.3.15 | Each feeder shall have two lock out relays powered through two independent DC supplies. Each lock out relay shall send through two separate potential free output contacts signals to each of the two independent trip coils. | Each feeder shall have two lock out relays powered through independent DC supplies. Each lock out relay shall send signals to the respective independent trip coils through separate potential free output contacts.
23 | SECTION - VII SUB-SECTION C | 16.2 Functional requirements | 165 of 354 | Subclause under 16.2.2 LCR/ICR | Building for installing inverter and associated equipment shall be of PEB (Pre-engineered building) type or RCC framed structure. Equipment inside LCR/ICR shall generally comprise of data loggers, battery, inverter, electrical panels, etc. as per requirements and as per approved system drawings. | Building for installing inverter and associated equipment shall be of PEB (Pre- engineered building) type or RCC framed structure. Equipment inside LCR/ICR shall generally comprise of data loggers, battery, inverter, electrical panels, etc. as per requirements and as per approved system drawings. Alternatively, in case outdoor rated equipment are proposed, the same shall be installed on RCC plinth as open installation. The plinth supporting the equipment shall have RCC framed structure with foundations, columns and beams built up to the plinth level(FFL). Open installations shall be provided with sheet metal canopy for weather protection. Structural members for the canopy shall be as per Cl 40: Pre-Engineered Building (PEB).
24 | SECTION - VII SUB-SECTION B | Part B: Battery Energy Storage System | 102 of 114 | Sub-section B 5.7 | Event logging / Digital data The control system shall provide for the automatic logging of the following information: | Event logging / Digital data The control system shall provide for the automatic logging of the following information (for a period of at least 6 months):
25 | SECTION - VII SUB-SECTION D | GENERAL ANNEXURE H SCADA Schematics and I/O List (Indicative) |  |  |  | Annexure Uploaded
26 | SECTION - VII SUB-SECTION B | Part A: Electrical System | - | 15.2.10 | New Clause | A virtual/cloud server running SCADA & Monitoring Software shall be configured in parallel with Plant Server to enable easy access to plant data from outside the plant without having to login to plant server. Effectively, the plant data shall be replicated in both places i.e. between systems at the Plant Server and Remote Server to provide data redundancy for complete plant data. Note: Configuration of Cloud server and procurement of associated subscription services shall be in the scope of the EPC Contractor.
27 | SECTION - VII SUB-SECTION E | SPECIFIC ANNEXURE SA-C - Geotechnical Investigation Report |  |  | New Annexure
28 | SECTION - VII SUB-SECTION E | SPECIFIC ANNEXURE SA-A: Tentative Land Layout |  |  |  | Updated Annexure Uploaded.
29 | SECTION - VII SUB-SECTION E | SPECIFIC ANNEXURE SA-D Topographical Survey Report |  |  | New Annexure
30 | SECTION - VII SUB-SECTION A | Scope of Works | 11 of 15 | 7.1 | Topographical survey of the plant area. | Topographical survey of the plant area. Note: Topographical survey report based on a past survey, including contour drawing is attached as Specific Annexure - SA-D. It may be noted that land development, grading and some construction works have been carried out at the site post the finalization of this survey report and hence, the bidder should expect variation in the site topography as per actuals. The report is provided only for reference and general information of the bidder. No warranty is expressed or implied that such information, given in good faith, will represent a complete or accurate picture of the whole of the site. The Employer shall not be responsible for any variation in topography, if observed, during detailed topographical survey to be carried out by the Contractor during contract execution and there shall be no compensation what so ever in the contract price on this.
31 | SECTION - VII SUB-SECTION A | Scope of Works | 11 of 15 | 7.2 | Geotechnical investigation of the plant area. For reference of bidder, general information regarding Geo-technical aspects of the site has been provided as Specific Annexure – SA-B. The Employer shall not be responsible for any variations in soil characteristics and other conditions, between those stated in SA-B, observed during preliminary site visit and detailed investigations to be carried out by the Contractor during contract execution and there shall be no compensation what so ever in the contract price on this account. | Geotechnical investigation of the plant area. For reference of bidder, general information regarding Geo-technical aspects of the site has been provided as Specific Annexure – SA-B. The Employer shall not be responsible for any variations in soil characteristics and other conditions, between those stated in SA-B, observed during preliminary site visit and detailed investigations to be carried out by the Contractor during contract execution and there shall be no compensation what so ever in the contract price on this account. Note: Geotechnical Investigation Report from an earlier study, including bore log, trial pit log, soil test results and ERT results is attached as Specific Annexure - SA-C. The bidder may use this report or conduct separate geotechnical investigation as deemed appropriate. The report is provided only for reference and general information of the bidder. No warranty is expressed or implied that such information, given in good faith, will represent a complete or accurate picture of the whole of the site. The Employer shall not be responsible for any variation in soil conditions, if observed, during any stage of project execution including detailed geotechnical investigation if carried out by the Contractor during contract execution and there shall be no compensation what so ever in the contract price on this.
32 | SECTION - VII SUB-SECTION F | O&M Agreement | - | Annexure-2 (2) | Annexure F | Updated Annexure Uploaded.
33 | SECTION - VII SUB-SECTION B | Part A: Electrical System | 4 of 114 | 1.2