## Pre Bid Queries
Tender for Design, Engineering, Supply, Construction, Erection, Testing, Commissioning and O&M of 12 MW (AC) Solar PV Power Plant System at Phey, Leh, UT of Ladakh, India
Tender No : SECI/C&P/PMC/11/03/2024-25
Sl. No. | Tender Section | Page No. | Clause No | Description as per Tender Document | Queries | Category (Finance/Technical/Contractual) | Clarifications
1 | SECTION – VII | 3 of 14 | 1 Project Particulars | Cumulative Power Transformer Capacity : 24 MVA (2 X 12 MVA) | Does the installed system transformer capacity should be 2 x 12 MVA or 1 x 12 MVA transformer to be used as per the project AC capacity. | Technical | 2 x 12 MVA. One number of transformer has been kept for redundancy.
2 |  |  |  | Metering Point | The Metering point is at plant end substation within boundary | Technical | Please refer Clause 1. Section VII - Scope of Works
3 |  |  |  | Minimum Guaranteed CUF to be maintained at 22.7% | The CUF to be maintained 22.7% during the O&M period or it has to be designed to maintain throughout 25 years. | Technical | It has to be designed for 25 years.
4 |  | 11 of 88 | 4.3 | 4.3 Technical Requirements Central inverter is mainly mentioned in tender documents. | Kindly clarify can string inverters can be used in this project. | Technical | The terms and conditions of the tender document shall prevail.
5 |  | 8 of 14 | 4.11 | 11 kV Internal Transmission Line along with towers, conductors, insulators as per relevant standards. | As the Design, Engineering, Supply, Construction, Erection, Testing, Commissioning of the contract is with the successful bidder can it be as per our design or it will be as per LPDD instruction. | Technical | It shall be as per LPDD approved drawings.
6 |  |  |  | Project boundary- Fencing | Kindly let us know the boundary fencing for the entire project site to be followed as per the fencing drawing provided in the tender document | Technical | Boundary fencing for the overall area is not in the scope of the bidder.
7 |  |  |  |  | Request you to kindly consider EMD/ Bid Security Exemption for MSME as Exemption id provide for only MSE | Contractual | EMD Exemption can be availed for MSE's in line with the terms specified in the tender document.
8 |  |  |  |  | Request you to kindly extend the bid submission date as, if the bid security is to be submitted as BG banks used to take minimum 15 Working days to issue it. Once we receive reply for our Pre bid queries, we request you to provided minimum 15 - 20 working days extension | Contractual | Kindly refer to SECI's website and ETS portal for extension details.
9 | SECTION - II | 19 | 5.3 | The Tender Processing Fee is exempted for MSEs Vendors registered under NSIC/Udyog Aadhar/ DIC Category only. | Is the EMD and Tender Processing Fees are exempted if the bidder is registered in MSME? | Contractual | EMD and Tender Processing Fees Exemption can be availed for MSE's in line with the terms specified in the tender document.
10 | SECTION - V | 155 | GCC clause 2.3 | The Contractor shall make own arrangements at his cost from the nearest supply source as per Owner terms and conditions, If Owner providing the water supply for construction & O&M activity. Construction water shall be chargeable as per the prevailing rate at respective site of the Owner. | If the water doesn’t meet the standards for cleaning or using, who shall purify the water before use? Bidder or Employer? | Technical | Water treatment/purification shall be in the scope of the bidder.
11 | SECTION - V | 153 | GCC clause 1, 3 | The Time for Commissioning for the project along with other associated equipment as per this tender document in total shall be 24 (Twenty-Four) Months from the Date of signing of Contract Agreement. | We would request you to kindly consider 30 months of Completion Period as the temperature goes below 0deg which ultimately affects the civil works like Cement doesn’t solidify at such temperature and it requires the summers time to solidly. Therefore, we would request you to kindly consider our request | Contractual | Kindly refer to Amendment 01.
12 | SECTION - V | 156 | GCC clause 24 | Contract Performance Security | We would request you to kindly consider the EMD and PBG issued to 1 entity only. | Contractual | The terms and conditions of the tender document shall prevail.

## Amendment 1
Tender No : SECI/C&P/PMC/11/03/2024-25
Tender for Design, Engineering, Supply, Construction, Erection, Testing, Commissioning and O&M of 12 MW (AC) Solar PV Power Plant System at Phey, Leh, UT of Ladakh, India
S. No. | Section | Sub-Section | Page No. | Clause | Original Version | Amendment
1 | SECTION - VII SUB-SECTION D | GENERAL ANNEXURE J Functional Guarantee (FG) Test Procedure | 4 of 9 | 2.1.2 | Eout: Cumulative Plant Generation measured at Plant End ABT meter over the duration of reporting period (kWh), (1/4) hour Tref : PV Module temperature at which P_o is determined, i.e. 25°C | Eout: Cumulative Plant Generation measured at the Metering Point over the duration of reporting period (kWh), (1/4) hour Tref: PV Module temperature averaged over the day, weighted by POA, i.e.: Tref = Σ (G_(i,k) * Tavg_mod,k ) / Σ G_(i,k)
2 | Section - VII | General Annexure-F: FG Test Procedure | 6 of 9 | 2.1.2 | (3) Estimation of Daily PR • For each reporting period (15-min time-block) of cumulative plant generation measured at plant end ABT meter, PR shall be calculated as per the formula given in Clause no. 2.1.2 | (3) Estimation of Daily PR • For each reporting period (15-min time-block), PR shall be calculated as per the formula given in Clause no. 2.1.2
3 | SECTION - VII SUB-SECTION B | Part A: Electrical System | 20 of 325 | 1.3 |  | Note: PV Module shall have been tested for design loads applicable at site (Refer TS-Civil, relevant clause on Design Load combinations) with minimum safety factor of 1.5 (as per IEC 61215-2) PV Modules shall conform to MNRE Order on Public Procurement (Preference to Make in India) to provide for Purchase Preference (linked with local content) in respect of RE Sector dated 9th February, 2021 and subsequent amendments.
4 | SECTION - VII SUB-SECTION B | Part A: Electrical System | 20 of 325 | 1.2
5 | SECTION - VII SUB-SECTION A | Scope of Works | 14 of 325 | 7.18 | Suitable arrangement of water shall be ensured to cater to day-to-day requirement of drinking water and permanent water supply for module cleaning (in case of wet type Module Cleaning System) and other needs of SPV power plant during entire O&M period. Please refer Sub-Section C: TS-Civil for further details. | Construction of wet type or dry type module cleaning system as per specifications. Suitable arrangement of water shall be ensured to cater to day-to-day requirement of drinking water and permanent water supply for module cleaning (in case of wet type Module Cleaning System) and other needs of SPV power plant during entire O&M period.
6 | SECTION - VII SUB-SECTION B | Part A: Electrical System | 100 of 325 | 23 .1 (ii) | (ii) Along the Plant Perimeter: Covering complete perimeter of Plant Area to capture all possible intrusion | (ii) Any strategic location in the Plant Area required to be monitored.
7 | SECTION - VII SUB-SECTION B | Part A: Electrical System | 100 of 325 | 23 .1 (ii) | (ii) Along the Plant Perimeter: Covering complete perimeter of Plant Area to capture all possible intrusion | (ii) Any strategic location in the Plant Area required to be monitored.
8 | SECTION - VII SUB-SECTION D | GENERAL ANNEXURE J Functional Guarantee (FG) Test Procedure | 6 of 9 | 2.1.4.2 (2) | Grid Interruptions – Time periods (15-minute time blocks) of the grid interruptions at the utility substation, recorded manually jointly by EPC Contractor and SECI representatives shall be eliminated. Grid outage period, if any, shall be verified from SCADA | Grid Interruptions – Time periods (15-minute time blocks) of the grid interruptions at the utility substation plus time for restoration (subject to a maximum of 30 minutes after grid is available subsequent to an interruption event) , recorded manually jointly by EPC Contractor and SECI representatives shall be eliminated. Grid outage period, if any, shall be verified from SCADA
9 | SECTION - VII SUB-SECTION B | Part A: Electrical System | 68 of 325 | 15.10.2 | Operating System and Database shall be of enterprise scale (RedHat Linux or equivalent Linux OS, Oracle/MySQL or Windows or equivalent DB), with required AMC for 5 years | Operating System and Database shall be of enterprise scale (OS - RedHat Linux or Windows Server or equivalent Linux OS; DB - Oracle/MySQL or Windows or equivalent DB), with required AMC for 5 years
10 | SECTION - VII SUB-SECTION C | TS-Civil, Mechanical and Plumbing Works | 145 of 325 | 24.2 | In MCR building, the supervisor room, Conference room and SCADA room shall have Hot and Cold type air conditioning units. | In MCR building, the supervisor room, Conference room and SCADA room shall have Air conditioning units.
11 | SECTION - VII SUB-SECTION C | 7. Surface/ Area drainage | 121 of 325 | 7.16 | The drain outfall shall be connected to the nearest existing natural drain(s)/ water body outside plant premises and it shall be ensured that the drainage water shall not re-enter the plant nor encroach/ flood in the adjacent property/ plot. | The plant drains shall be connected to the nearest existing natural drain(s) inside the plant area which are finally draining the water outside the plant. Such existing natural drains shall be cleaned and developed propel to facilitate effective drainage. The contractor may also propose for recharge pits of adequate size and in adequate numbers to meet the requirement of storm water disposal.
12 | SECTION - VII SUB-SECTION D | General Annexure I: Plant Documentation, Commissioning & Test Procedure | Page 16 of 21 | 6 | Battery Energy Storage System | Void
13 | SECTION - VII SUB-SECTION B | Part A: Electrical System | 85 of 325 | 19.3.15 | Each feeder shall have two lock out relays powered through two independent DC supplies. Each lock out relay shall send through two separate potential free output contacts signals to each of the two independent trip coils. | Each feeder shall have two lock out relays powered through independent DC supplies. Each lock out relay shall send signals to the respective independent trip coils through separate potential free output contacts.
14 | SECTION - VII SUB-SECTION C | 16.2 Functional requirements | 165 of 354 | Subclause under 15.2.2 LCR/ICR | Building for installing inverter and associated equipment shall be of PEB (Pre-engineered building) type or RCC framed structure. Equipment inside LCR/ICR shall generally comprise of data loggers, battery, inverter, electrical panels, etc. as per requirements and as per approved system drawings. | Building for installing inverter and associated equipment shall be of PEB (Pre- engineered building) type or RCC framed structure. Equipment inside LCR/ICR shall generally comprise of data loggers, battery, inverter, electrical panels, etc. as per requirements and as per approved system drawings. Alternatively, in case outdoor rated equipment are proposed, the same shall be installed on RCC plinth as open installation. The plinth supporting the equipment shall have RCC framed structure with foundations, columns and beams built up to the plinth level(FFL). Open installations shall be provided with sheet metal canopy for weather protection. Structural members for the canopy shall be as per Cl 40: Pre-Engineered Building (PEB).
15 | SECTION - VII SUB-SECTION F | O&M Agreement | - | Annexure F | Annexure F | Updated Annexure Uploaded.
16 | SECTION - VII SUB-SECTION B | Part A: Electrical System | - | 15.2.10 | New Clause | A virtual/cloud server running SCADA & Monitoring Software shall be configured in parallel with Plant Server to enable easy access to plant data from outside the plant without having to login to plant server. Effectively, the plant data shall be replicated in both places i.e. between systems at the Plant Server and Remote Server to provide data redundancy for complete plant data. Note: Configuration of Cloud server and procurement of associated subscription services shall be in the scope of the EPC Contractor.
17 | Annexure to BDS - QR | 1.3 FINANCIAL ELIGIBILITY CONDITIONS | 5 of 10 | 1.3 | The bidder should have a minimum Working Capital of INR 11,12,00,000/- (Indian Rupees Eleven crores Twelve lakhs only) as per the last audited financial statement. If the bidder’s working capital is inadequate, the bidder should supplement this with a letter from the bidder’s bank, having net worth not less than INR 500 Crores, confirming availability of the line of credit for more than or equal to INR 11,12,00,000/- (Indian Rupees Eleven crores Twelve lakhs only) to meet the working Capital requirement of this particular Project. | The bidder should have a minimum Working Capital of INR 7,41,00,000/- (Indian Rupees Seven crores Forty One lakhs only) as per the last audited financial statement. If the bidder’s working capital is inadequate, the bidder should supplement this with a letter from the bidder’s bank, having net worth not less than INR 500 Crores, confirming availability of the line of credit for more than or equal to INR 7,41,00,000/- (Indian Rupees Seven crores Forty One lakhs only) to meet the working Capital requirement of this particular Project.
18 | Section V Special Conditions of Contract | Timeline | 2 of 10 | 3 | The Time for Commissioning for the project along with other associated equipment as per this tender document in total shall be 24 (Twenty-Four) Months from the Date of signing of Contract Agreement. | The Time for Commissioning for the project along with other associated equipment as per this tender document in total shall be 36 (Thirty-Six) Months from the Date of signing of Contract Agreement.
19 | Section V Special Conditions of Contract | Timeline | 2 of 10 | 3.2 | Date of Successful Commissioning : D + 24 Months | Date of Successful Commissioning : D + 36 Months
20 | Section V Special Conditions of Contract | Contract Performance Security | 5 of 10 | 9 | First Stage (Supply and Services): The value of the Contract Performance Security shall be 5% (Five percent) of the Contract Value (i.e., total sum of the Supply & Service Contract). This Performance security will be valid for a total period of 87 Months (24 Months Project commissioning period) + prescribed O & M Period, i.e., 60 Months + 03 Months additional) from the date of its issuance. The successful bidder can submit Contract Performance Security with initial validity of 36 months and the same may be extended after every 36 months till completion of the total 87 months period. | First Stage (Supply and Services): The value of the Contract Performance Security shall be 5% (Five percent) of the Contract Value (i.e., total sum of the Supply & Service Contract). This Performance security will be valid for a total period of 99 Months (36 Months Project commissioning period) + prescribed O & M Period, i.e., 60 Months + 03 Months additional) from the date of its issuance. The successful bidder can submit Contract Performance Security with initial validity of 36 months and the same may be extended after every 36 months till completion of the total 99 months period.