## Pre Bid Clarifications
“THE MANUFACTURING, TESTING, PACKING AND FORWARDING, SUPPLY AND TRANSPORTATION OF 400 MWP DOMESTICALLY MANUFACTURED SOLAR PV MODULES WITH DOMESTICALLY MANUFACTURED SOLAR CELLS”
Tender No : SECI/C&P/OP/11/016/2024-25
Sl. No. | Tender Section | Page No. | Clause No | Description as per Tender Document | Queries | Category (Finance/Technical/Contractual) | Clarifications
1 | SECTION - IV | GPC Page 40 of 44 | 69.8 | Owner shall be named as co – insured under all insurance policies taken out by the Supplier, except for the workmen compensation, third party liability and Owner’s liability insurances | Insurance certificates for example warranty insurance certificate will be issued in the name of owner (SECI), as most of insurance policies have already been subscribed in the name of supplier and same are utilized for various client. Other insurance policies are also purchased on supplier's name only. Request to accept accordingly. | Contractual | The terms and conditions of the tender document shall prevail.
2 | SECTION - VII PART – B: TECHNICAL SPECIFICATIONS | SoS & TS Page 5 of 19 |  | IS/IEC 61701: 2011: Salt Mist Corrosion Testing of Photovoltaic (PV) Modules – Severity 1 | Kindly confirm if manufacturer has- Severity - 6 test certificate as per IEC 61701: 2020. will it be acceptable? | Technical | The required standard represents the minimum requirement for compliance. Since Severity-6 exceeds the minimum requirements, it is deemed acceptable and suitable for the intended application.
3 | SECTION - VII PART – B: TECHNICAL SPECIFICATIONS | SoS & TS Page 7 of 19 | 4.7 (iii) | RFID details requires "Type of cell" | This details is usually not included in the RFID data. We request to remove the requirement of "Type of cell" from RFID. | Technical | Please refer S. No. 1 of Amendment.
4 | SECTION - VII PART – B: TECHNICAL SPECIFICATIONS | SoS & TS Page 7 of 19 | 4.3 | Encapsulant Type: (ii) Glass/Glass Modules – POE on Front side | We have multiple certified encapsulant combinations having EVA and EPE on front. We request to allow other encapsulants for usage as well. | Technical | Please refer S. No. 2 of Amendment.
5 | SECTION - VII PART – B: TECHNICAL SPECIFICATIONS | SoS & TS Page 9 of 19 | 7.3 | Current binning of modules shall be employed so that current mismatch of modules in a pallet does not exceed 150 mA at Maximum Power (Imp). Different colour codes shall be provided on the modules as well as pallet for identification of different bins. The Supplier shall submit the binning scheme to the Employer for approval, prior to manufacturing. | We request to remove the requirement of current binning and color coding. We can sort the module based on power only as different bins will create different stacks and add complexity in manufacturing process. All the related details to the modules are mentioned over the packing list on every packaging box. Single Wp bin module are packed in a pallet. | Technical | The terms and conditions of the tender document shall prevail.
6 | SECTION - VII PART – B: TECHNICAL SPECIFICATIONS | SoS & TS Page 9 of 19 | 7.4 | The Manufacturing shall start only after the clearance by the Owner after the material inspection. | Manufacturing will start as per the mutually agreed schedule of the production between supplier & buyer and inspection has to be done agreed timelines. Please remove this clause as it will add complexity and it will delay the manufacturing. | Technical | Please refer S. No. 3 of Amendment.
7 | SECTION - VII PART – C: PRE-DISPATCH INSPECTION PROTOCOL | SoS & TS Page 12 of 19 | 6-Sampling Process | Flash Test, Visual Inspection, Electroluminescence | Please consider- Inspection Level : Special inspection level S4. | Technical | The terms and conditions of the tender document shall prevail.
8 | SECTION - VII PART – B: TECHNICAL SPECIFICATIONS | SoS & TS Page 6 of 19 | 3 | The PV Module dimensions at the time of Supply shall be fixed as per details provided in Form T-01 submitted along with the bid. | Is it possible to participate with two dimension of modules? We are intending to apply with 2 different types of modules having different dimensions. | Technical | No, the terms and conditions of the tender document shall prevail.
9 | Section V- Special Purchase Conditions | SPC Page 2 of 9 | 3.1 to 3.5 | -Issue of Contract Agreement / Purchase & Service Order (as applicable)-Zero Date (D) '-Submission of Drawing and Test Certificates-D + 10 days -Submission of PAN File-D + 20 days | Request to allow the submission of Test Certificate and PAN File - prior to delivery (supply )start date. | Contractual | To be amended as per Clause 1.5 of Scope of Supply( 60 days from LOA)
10 | SECTION-I INVITATION FOR BIDS (IFB)/BID INFORMATION SHEET | 13 of 15(16/226) | L | ONLINE BID-SUBMISSION DEADLINE - 05.12.2024 up to 1400 HRS | EMMVEE Requests to Extend the Bid Submission dates by 4-WEEKS AND provide new date with 02.01.2025 | Contractual | The bid submission deadline, if extended, will be reflected on SECI's website and ETS portal.
11 | SECTION-III BID DATA SHEETS (BDS) | 72 | BID VALIDITY (ITB 14.1) | Bid Validity-The bid validity period shall be 180 (One Hundred and Eighty Days) from the date of opening of Techno Commercial Bid (Envelope-I). | EMMVEE request to amend BID VALIDITY period to 90-days from date of opening of Techno-commercial bid (Enevelop-1) | Contractual | The terms and conditions of the tender document shall prevail.
12 | SECTION - V SPECIAL PURCHASE CONDITIONS (SPC) | 7 of 9 (133/226) | SPC No.-13/ Schedule of Rates & Payments (GPC clause 78) | Schedule of Rates & Payments Terms of 10%, 80% & 10% | SECI to Confirm the LC will be for 100 % of the Contract Value including GST. Emmvee Request for 10% advance and balance 90% payment through irrevocable Letter of Credit for 30 days from the date of Tax Invoice with usance interest to account of SECI. EMMVEE request you to establish an irrevocable Letter of Credit (L/C) in favour of the supplier through the Employer's Bank for payments. | Contractual | The terms and conditions of the tender document shall prevail.
13 | SECTION-I INVITATION FOR BIDS (IFB)/BID INFORMATION SHEET | 16 of 226 | J | CONTRACT PERFORMANCE SECURITY - 10% of the Total Project/Order Cost for a total period of 24 months. | We request you to amend CONTRACT PERFORMANCE SECURITY to 3% of the Total Project/Order Cost for a total period of 24 months. | Contractual | The terms and conditions of the tender document shall prevail.
14 | SoS & TS | 5 of 19 - (210 of 226) | PART – B: TECHNICAL SPECIFICATIONS - 2 Standards | IS 14286 (Part 1)-2019 - Terrestrial Photovoltaic (PV) Modules - Design Qualification and Type Approval, Part 1: Test Requirements (Second Revision) | IS 14286 (Part 1) – 2019-is equivalent IEC 61215-2016. Our modules are qualified IEC 6125-2021 which is superior and latest version as compared to 2016. Also we comply to IS14286 -2010. There is no CRS scheme available in BIS portal for the latest IS 14286:2019 | Technical | Higher revisions of standards are acceptable.
15 | SoS & TS | 5 of 19 - (210 of 226) | PART – B: TECHNICAL SPECIFICATIONS - 2 Standards | IS 14286: Part 1: Sec 1: 2019 - Terrestrial Photovoltaic (PV) Modules - Design Qualification and Type Approval, Part 1: Test Requirements, Section 1: Special requirements for testing of crystalline silicon photovoltaic (PV) modules (Second Revision) | IS 14286 (Part 1/Sec1) – 2019-is equivalent IEC 61215(Part 1/Sec 1)-2016. Our modules are qualified IEC 6125-2021 which is superior and latest version as compared to 2016. Also we comply to IS14286 -2010. There is no CRS scheme available in BIS portal for the latest IS 14286:2019. | Technical | Higher revisions of standards are acceptable.
16 | SoS & TS | 7 of 19 - (210 of 226) | PART B: TECHNICAL SPECIFICATIOS - 4 Component Specifications | 4.3 - Encapsulant Type ii) Glass/Glass Modules – POE on Front side | Encapsulant Type - ii) Glass/Glass Modules – EPE on Front side & EPE on rear side | Technical | Please refer S. No. 2 of Amendment.
17 | SOS &TS | 8 of 19 - (213 of 226) | PART B: TECHNICAL SPECIFICATIONS 5 Warranty - 5.1 Performance Warranty | 5.2 PV Modules shall be warranted for power output, as specified by the bidder in the Degradation Curve, for a minimum period of 25 years commencing from the date of the last Tax invoice raised under the contract. | Please clarify the same shall be applicable from the date of Tax Invoice | Technical | It is clarified that the same shall be applicable from the date of last Tax Invoice.
18 | SOS &TS | 8 of 19 - (213 of 226) | PART B: TECHNICAL SPECIFICATIONS 5 Warranty - 5.4 Warranty Insurance | 5.5 The Supplier under this Contract (i.e. the Insurer) shall purchase an Insurance Policy (i.e. Buyer's cover) to insure it's contractual liabilities arising out of the long-term performance and product warranties as per Clause above on PV Modules to be supplied to the buyer (i.e. Beneficiary - SECI) under the Contract. The aggregate limit of Insurer's liability under this Policy in respect of all Photovoltaic Modules covered under this Policy during the Policy Period shall be 6% of the Total Sum Insured, where Total Sum Insured shall be the total Invoice Value of capacity awarded under this Contract. This insurance should be valid for a period of 25 years from the date of last Tax Invoice under the contract and the claim period should extend for a minimum of 1 year beyond this date. Warranty Insurance certificate shall clearly identify the Beneficiary (i.e. SECI) along with project details viz. Location, Total Sum Insured and relevant contract reference details. | This insurance should be valid for a period of 25 years from the date of Tax Invoice, and the claim period should extend for a minimum of 1 year beyond this date is not acceptable/agree. | Technical | The terms and conditions of the tender document shall prevail.
19 | SOS &TS | 9 of 19 - (214 of 226) | PART B: TECHNICAL SPECIFICATIONS 7 Manufacturing and Inspection | 7.3 Current binning of modules shall be employed so that current mismatch of modules in a pallet does not exceed 150 mA at Maximum Power (Imp). Different colour codes shall be provided on the modules as well as pallet for identification of different bins. The Supplier shall submit the binning scheme to the Employer for approval, prior to manufacturing | No color code on the modules, only identification label I1/I2/I3 on the modules & boxes will be provided to identified the current class or Bins. Min of 3 bins with 150mA range of 1st bin and last bin shall be open, centre bin will be closed | Technical | The terms and conditions of the tender document shall prevail.
20 | SOS &TS | 11 of 19 - (216 of 226) | PART – C: PRE-DISPATCH INSPECTION PROTOCOL 5.1 BOM verification | 5.1 BOM verification - The details of materials used will be verified from the ERP/Manufacturing data and corroborated with the approved Bill of Materials. | Please note that verification from ERP is not industry practice, The details of materials used for the production shall be verified during the BOM verification at the shop floor. | Technical | Supplier shall provide documentary evidence/production records in support of Bill of Materials used, validity of shelf life of the Materials (as applicable) etc. Provision of the same from Manufacturer's ERP data is optional.
21 | SOS &TS | 12 of 19 - (217 of 226) | PART – C: PRE-DISPATCH INSPECTION PROTOCOL 6.0 Sampling Process | Flash Test - General inspection level I | Special Inspection Level S-4 | Technical | Refer S. No. 5 of Amendment
22 |  |  |  | Visual Inspection -General inspection level I | Special Inspection Level S-4 | Technical | Refer S. No. 5 of Amendment
23 |  |  |  | Electroluminescence-General inspection level I | Special Inspection Level S-4 | Technical | Refer S. No. 5 of Amendment
24 | SOS &TS | 13 of 19 - (218 of 226) | PART – C: PRE-DISPATCH INSPECTION PROTOCOL 8 Inspection Process | 8.2 Visual Inspection-The inspector(s) shall visually verify characteristics of PV Module as per the Visual Inspection Criteria | As per the Emmvee Visual inspection criteria. | Technical | Visual Inspection Criteria shall be agreed with the Supplier prior to Pre-dispatch Inspection
25 | SOS &TS | 13 of 19 - (218 of 226) | PART – C: PRE-DISPATCH INSPECTION PROTOCOL 8 Inspection Process | 8.3 Electroluminescence (EL) Inspection- The inspector(s) shall visually verify characteristics of PV Module as per the Visual Inspection Criteria | As per the Emmvee EL inspection Criteria. | Technical | Electroluminescence Criteria shall be agreed with the Supplier prior to Pre-dispatch Inspection
26 | SOS &TS | 14 of 19 - (219 of 226) | PART – C: PRE-DISPATCH INSPECTION PROTOCOL 11 Disclaimer | Inspection by Owner or its authorized inspection agency does not absolve the responsibility of the Supplier to ensure quality during production of the material and its transport to site. Any damages during transport/ handling shall be replaced without any extra cost to the Owner. | If any damage during it transport/ handling shall be informed to the transporter or LR and with in concealment period mutually agreed by the both party | Technical | Please refer Clause 1.1 of the Scope of Work requiring that "..the Supplier shall depute an authorized representative to the site commencing from the date of delivery of first consignment till the completion of all Supplies under this Contract for verification of receipt of the consignment in good condition, and to facilitate the handing over of the same to the Employer/Employer's assignee." Damages during transport/handling shall be informed to the Supplier authorized representative.
27 | SPC | 7 of 9 - (133 of 226) | 10 - 53.2.13 Latent Defect Liability | Add following to the existing clause: 53.2.13 Latent Defect Liability: Notwithstanding, the defect liability period of 12 months above, the contract shall carry a latent defect liability of 5 years from date of delivery of material at site towards any defects in the modules supplied by the Supplier. | Please delete Latent Defect Liability clause, as latent Defect liability is NOT applicable as per prevailing industry norms. | Contractual | The terms and conditions of the tender document shall prevail.
28 | BID DATA SHEETS (BDS) | 3 of 4 - (72 of 226) | 7 - Zero deviation & Rejection Criteria | Clause No. 18.1, Zero deviation & Clause No. 18.2, Rejection Criteria should be read in conjunction to each other & both clauses points mentioned should complement each other. | Unavoidable Deviations should be Allowed. | Contractual | The terms and conditions of the tender document shall prevail.
29 | General | - | - | - | We request you to incorporate De-Loading Factor in the Bid Evaluation so that higher Wp ratings {580 Wp – 590 Wp} which result in BOS savings get evaluated fairly w.r.t lower Wp ratings {540 Wp -550 Wp} | Technical | The terms and conditions of the tender document shall prevail.
30 | SPC | Page 8 of 9 | Clause No. 13 (Schedule of Rates & Payments) | A. The payment against Supply portion shall be made as per the following terms and conditions: i) Interest bearing advance of 10% of the total value of Supply portion shall be released to supplier against Submission of Test Certificates / Manufacturing Clearance, detailed Performa invoice of contractor and against submission of unconditional & irrevocable Advance Bank Guarantee (ABG) with a validity period up to date of final supply amounting to 110% of total advance amount. The ABG needs to be submitted in addition to the Contract Performance Security. The annual interest rate shall be calculated based on SBI one-year MCLR as applicable. ii) Eighty percent (80%) of the total value of Supply portion shall be paid upon dispatch of Solar PV Modules (along with mandatory spares) from manufacturer's works on pro-rata basis on production of invoices and satisfactory evidence of shipment which shall be original Goods Receipt or receipted GR/Rail Receipt including Material Dispatch Clearance Certificate (MDCC) issued by the Owner’s Corporate QA & I representative and copy of Insurance for the supplied goods issued by the Supplier....................................... | We would like to request amendments to the payment terms as per the tender clause, with the following justification: Increase in Advance Payment: a. Due to the significant working capital shortage that manufacturers are currently facing, we request an increase in the advance payment from 10% to 20%. b. As this is a fixed-price contract, we will need to procure the entire wafer upon the award of the contract. The higher advance will enable us to manage these procurement costs efficiently. c. We also propose an amendment to the clause to make the advance payment interest-free, instead of the current interest-bearing advance. Adjustment in the Bank Guarantee (ABG): We request that the ABG amount be revised from 110% to 100% of the advance amount. This adjustment would be in line with industry practices and would alleviate some of the financial strain on the suppliers. Also, modification to the Remaining Payment Terms: We kindly request that the remaining 80% of the payment be made via a Letter of Credit (LC) instead of the current arrangement. We believe that these adjustments will result in more competitive and favourable pricing in the bid, benefiting all parties involved. | Contractual | The terms and conditions of the tender document shall prevail.
31 | SPC | Page 3 of 9 | 6. Contract Performance Security (GPC clause 25) | 25.1 The value of the Contract Performance Security shall be 10% (Ten) of the Contract Value (i.e., total sum of the Supply & Service Contract). This Performance security will be valid for a total period of 24 Months (9 Months Project completion period) + 12 months of Defect Liability Period + 03 Months additional) from the date of its issuance. | We request that the CPG be revised to 5% of the total contract value, in line with industry norms. A 5% CPG is widely accepted by PSUs, including in recent tenders by NTPC and NLC. | Contractual | The terms and conditions of the tender document shall prevail.
32 | BDS | Page 3 of 4 | Sl No. 6 (BID VALIDITY) | The bid validity period shall be 180 (One Hundred and Eighty Days) from the date of opening of Techno-Commercial Bid (Envelope-I). | Wafer is the key component of this project and the Market price of wafer is highly volatile, request you to kindly consider for 60/90 days. | Contractual | The terms and conditions of the tender document shall prevail.
33 | General | - | - | Minimum and maximum Wp of module | Please clarify if there is any minimum or maximum Wp of modules required. | Contractual | The bidders must supply Module with minimum wattage of 540 Wp. However there is no upper ceiling on wattage type.
34 | General | - | - | Price variation | Please include Price variation | Contractual | The terms and conditions of the tender document shall prevail.
35 | SECTION – VII SoS & TS | Page 5 of 18 | 3 Technical Requirements | Power Rating at STC ≥ 540 Wp | We request you to kindly consider the Min. wattage supply can be 530/ 535Wp instead of 540Wp | Technical | The terms and conditions of the tender document shall prevail.
36 | SECTION - VII | SoS & TS Page 6 of 19 | 4.1.1 | PART – B: TECHNICAL SPECIFICATIONS Glass/Glass Modules: Glass shall have minimum 2 mm thickness on each side. | Glass used will be 2mm thickness with a manufacturing tolerance of -/+ 0.2mm | Technical | The terms and conditions of the tender document shall prevail.
37 | SECTION - VII | SoS & TS Page 5 of 19 | 2.1 | IS/IEC 61701: 2011 - Salt Mist Corrosion Testing of Photovoltaic (PV) Modules – Severity 1 | IS/IEC 61701: 2011 - Salt Mist Corrosion Testing of Photovoltaic (PV) Modules – Severity 6 can be accepted | Technical | The required standard represents the minimum requirement for compliance. Since Severity-6 exceeds the minimum requirements, it is deemed acceptable.
38 | SECTION - VII | SoS & TS Page 7 of 19 | 4.3 | Encapsulant Type For TOPCon Modules: (i) Glass/backsheet Modules - POE or EPE on both front and back sides of the cell ii) Glass/Glass Modules – POE on Front side | Encapsulant Type For TOPCon Modules: ii) Glass/Glass Modules – POE/EPE on Front side & POE/EPE/EVA on back side | Technical | Please refer S. No. 2 of Amendment.
39 | SECTION - VII | SoS & TS Page 9 of 19 | 7.3 | Current binning of modules shall be employed so that current mismatch of modules in a pallet does not exceed 150 mA at Maximum Power (Imp). | Current binning to be removed & only Pmax binning. 2 to 3 bins of Pmax of 0~4.99Wp are acceptable. | Technical | The terms and conditions of the tender document shall prevail.
40 | SECTION - VII | SoS & TS Page 9 of 19 | 7.6 | The Owner shall perform material inspection at the Manufacturer’s factory before the start of proposed manufacturing schedule. | Raw material inspection to be waived off, however we can submit the inspection documents. | Technical | Please refer S. No. 4 of Amendment.
41 | SECTION - VII | SoS & TS Page 12 of 19 | 6(i) | PART – C: PRE-DISPATCH INSPECTION PROTOCOL - Sampling process Visual Inspection - General inspection level I | PART – C: PRE-DISPATCH INSPECTION PROTOCOL - Sampling process Visual Inspection - Special inspection level 4 (S4) since to handle manually G1 qty is too high | Technical | Please refer S. No. 5 of Amendment.
42 | SECTION - V | SPC Page 8 of 9 | 13 | SPECIAL PURCHASE CONDITIONS (SPC) - Schedule of Rates & Payments (GPC clause 78) The payment against Supply portion shall be made as per the following terms and conditions: i) Interest bearing advance of 10% of the total value of Supply portion shall be released to supplier | i) Interest free advance of 10% of the total value of Supply portion shall be released to supplier | Contractual | The terms and conditions of the tender document shall prevail.
43 | SECTION - V | SPC Page 8 of 9 | 13 | Eighty percent (80%) of the total value of Supply portion shall be paid upon dispatch of Solar PV Modules (along with mandatory spares) from manufacturer's works on pro-rata basis on production of invoices and satisfactory evidence of shipment which shall be original Goods Receipt | LC payment is recommended | Contractual | The terms and conditions of the tender document shall prevail.
44 | Section-I IFB | 6 of 15 | 4.0 Public Procurement Policy | A Class-I local supplier' means a Supplier or Service Provider, whose Goods, Services or works offered for Procurement, has local content equal to or more than 50%, as defined under the above said orders. | We request SECI to clarify whether Wafers and Cell Line BoM items which are used in the manufacturing of DCR or Domestically Manufactured cells also fall under this category? According to our understanding, 50% of the raw materials being procured for manufacturing of Solar Modules needs to be sourced from India. Since DCR cells (with Chinese Wafers and Chinese Cell BoM) is more than 50% of the module cost, such modules would qualify under Class-I local supplier. | Contractual | The bidder must ensure that the Cell Manufacturer and the Module Manufacturer must comply with the DCR norms.
45 | Section-VI Sample Forms and Formats | 17 of 59 | Form F-8 | Bidder's Experience | We request SECI to provide clarity on how far back in time can we represent the relevant documents? For instance, can we show relevant orders 4 to 5 years prior to bid submission date of 05.12.2024 | Contractual | It is advised to submit most recent orders secured by the organization meeting the Technical Eligibility Conditions as per the quoted package capacity.
46 | SECTION – VII SCOPE OF SUPPLY & TECHNICAL SPECIFICATIONS | 5 of 19 | Part B; Clause 2 Standards | Photovoltaic Modules shall comply with the specified edition of the following standards or equivalent IEC standards | We interpret that only compliance to BIS standards shall suffice and there is no need to provide equivalent IEC certifications. Kindly clarify. | Technical | The Supplier shall comply with all technical specifications, including Codes and Standards, as per the tender document. The terms and conditions of the tender document shall prevail.
47 | SECTION – VII SCOPE OF SUPPLY & TECHNICAL SPECIFICATIONS | 5 of 19 | Part B; Clause 2 Standards | Photovoltaic Modules shall comply with the specified edition of the following standards or equivalent IEC standards | If compliance to BIS Standards shall suffice, kindly note that BIS standards permit multiple suppliers/ make to used for each Module Bill of Materials (BoM) and in any combination. SECI to confirm whether this is acceptable. | Technical | Please refer Clause 6: Approval of the Technical Specifications.
48 | SECTION – VII SCOPE OF SUPPLY & TECHNICAL SPECIFICATIONS | 7 of 19 | Part B; Clause 4.3 | Encapsulant - EVA for PERC Bifacial Modules | We request SECI to permit use of EPE or EVA or combination of both for M10 PERC Bifacial Modules. | Technical | Please refer S. No. 2 of Amendment.
49 | SECTION – VII SCOPE OF SUPPLY & TECHNICAL SPECIFICATIONS | 11 of 19 | Part C; Clause 4.3 | PRE-DISPATCH INSPECTION PROTOCOL | We request SECI to clarify the scope of appointment of inspection agency and the cost associated with it. | Technical | Pre-Dispatch Inspection of Lots to be suppled under the Contract, at the Supplier's facility, shall be in the Scope of SECI.
50 | SECTION – VII SCOPE OF SUPPLY & TECHNICAL SPECIFICATIONS | 6 of 19 | Part B; Clause 3 Technical Requirements | Power Rating at STC ≥540Wp | We request SECI to permit supply of modules greater than 540Wp and accordingly adjust the selling price according to Wp. So, 545Wp will be sold at a proportionately higher price compared to 540Wp, while Rs/Wp remains the same. | Technical | Supply of Modules greater than 540 Wp is acceptable as per the Clause.
51 | SECTION – VII SCOPE OF SUPPLY & TECHNICAL SPECIFICATIONS | 6 of 19 | Part B; Clause 3 Technical Requirements | Mechanical Load requirements | We request SECI to confirm the mechanical load requirements for the module. Also to confirm whether module shall be installed on Tracker or Fixed Mounted. | Technical | Module shall be Fixed Type. Mechanical Load requirements shall be as per IEC Standards.
52 | - | - | - | General | Please confirm bidders needs to supply modules from its own manufacturing plant or a bidder can do OEM in others company manufacturing plant with modules in its name for supply under this contract | Contractual | Bidders are required to supply modules from they existing manufacturing facility under production. However in exceptional and exigent cases & with the prior approval of the owner, the Module Supplier may also source the Modules, from some other Domestic Module producer having domestic cells complying the mentioned ALMM & Technical requirements as laid down in the tender document. However, all such cases may be adopted in the exceptional & urgent situations only, exceptionality of which may be duly justified and put on records for the prior approval of the Owner.
53 | - | - | - | General | Subcontracting clause is mentioned in the tender, please clarify sub contracting means a bidder can supply modules of other brands also . | Contractual | Bidders are required to supply modules from they existing manufacturing facility under production. However in exceptional and exigent cases & with the prior approval of the owner, the Module Supplier may also source the Modules, from some other Domestic Module producer having domestic cells complying the mentioned ALMM & Technical requirements as laid down in the tender document. However, all such cases may be adopted in the exceptional & urgent situations only, exceptionality of which may be duly justified and put on records for the prior approval of the Owner.
54 | SoS & TS | 208 | 1.1 | Unloading of modules at site is in the scope of bidders | As per prudent practise We request SECI to remove unloading of modules from the manufacturers scope and keep in the BOS/EPC contractor scope | Contractual | Unloading of Modules is not under the scope of supplier. However the supplier must assist the owner and the BoS Contractor through a deployed Project In charge during the process of unloading and inspection.
55 | IFB | 15 | (I) | EMD | We request SECI to accept Bid security declaration in place of EMD as per the | Contractual | The terms and conditions of the tender document shall prevail.
56 | ITB | 48 | V | Mechanism for L1 matching: | Please clarify, the in RA only L1 bidder will be awarded the Quoted Capacity, Other bidder from L2, L3… need to match the L1 Price if any balance capacity is left after L1 Awarded Capacity as the same is not clear in the tender clauses. | Contractual | The process followed will be Bucket Filling along with the provision of L1 Matching. For ex.: If 3 (L1,L2,L3) bidders emerged as successful supplier at the end of e-RA, then post the e-RA both the L2 and L3 will be given an offer to match the L1 price and so on.
57 | BDS | 72 | Sl 6 | Bid Validity - 180 days from opening of Envelope 1 (Techno-Commercial Bid) | We request SECI to make the bid validity as 90 days from Opening of Envelope 1, ADD, | Contractual | The terms and conditions of the tender document shall prevail.
58 | ANNEXURE TO BDS | 78 | 1.2 | A summarized sheet of average turnover, certified by a practicing Chartered Accountant/Statutory Auditor should be compulsorily enclosed along with corresponding annual accounts. | Bidder is already submitting balance sheet containing all the details and breakup, additional requirement of Certificate from practicing Chartered Accountant/Statutory Auditor is an unnecessary requirement. Pls remove this requirement. | Contractual | The terms and conditions of the tender document shall prevail.
59 | SPC | 133 | 53.2.13 | Latent defect- 5 years | Latent Defect should be in concurrence to DLP, 12 months from invoice, pls accept | Contractual | The terms and conditions of the tender document shall prevail.
60 | 52 | 114 | 53.2 | 12 (Twelve) Months Period of Liability from the date of material delivery at site] | Date of invoice is the Warranty start date | Contractual | The terms and conditions of the tender document shall prevail.
61 | SPC | Page 9 of 9 | 134 | Payment terms- Interest Bearing advance | Kindly make it interest free advance | Contractual | The terms and conditions of the tender document shall prevail.
62 | SPC | Page 9 of 9 | 78 | Payment terms | Please also have provision to make the payment through Letter of Credit | Contractual | The terms and conditions of the tender document shall prevail.
63 | 53.2 | 114 | 53.2.2 | The decisions of the Project Manager in this regard shall be final and binding. | mutual decision will be taken followed by the proper Root Cause Analysis. | Contractual | The terms and conditions of the tender document shall prevail.
64 | 54 | 115 | 54 | If at any time, before the Supply is taken over, the Engineer-in-Charge/Project Manager shall: a) Decide that any supply done or materials used by the Supplier or by any Sub-Supplier is defective or not in accordance with the Contract, or that the supply or any portion thereof are defective, or do not fulfil the requirements of Contract (all such matters being hereinafter, called `Defects' in this clause), and | During the warranty period if any defects being observed, proper RCA shall be done, and Remedy will be provided by mutual decision as per VSL warranty manual. | Contractual | The terms and conditions of the tender document shall prevail.
65 | SoS & TS | 210 | 2.1 | IS 17210: Part 1: 2019/ IEC TS 62804-1 : 2015 | Complied with IEC 61215:2021 | Technical | Bidder shall comply to mentioned IS standards or equivalent IEC standards.
66 | SoS & TS | 210 | 2.1 | IS 16664: 2018 Photovoltaic (PV) Modules- Ammonia Corrosion Testing | Complied with IEC 62716 | Technical | Bidder shall comply to mentioned IS standards or equivalent IEC standards.
67 | SoS & TS | 210 | 2.1 | IS 17210: Part 1: 2019 Photovoltaic (PV) Modules - Test Methods for the Detection of Potential-Induced Degradation, Part 1: Crystalline Silicon (under conditions of 85°C/85% RH for minimum 192 hours) | Complied with IEC 62804 | Technical | Bidder shall comply to mentioned IS standards or equivalent IEC standards.
68 | SOS &TS | 6 of 18 - 211 | PART B: TECHNICAL SPECIFICATIONS - 4 Component Specifications | 4.2 Back Sheet - The Owner reserves the right to conduct Pressure Cooker (PC) test/ Highly Accelerated Stress Test (HAST) to confirm the durability of the back sheet in accelerated conditions | Pressure Cooker (PC) test will be conduct at external lab and cost will borne by Employer. Please confirm. | Technical | The terms and conditions of the tender document shall prevail.
69 | SOS &TS | 11 of 18 - 217 | PART – C: PRE-DISPATCH INSPECTION PROTOCOL 8 Inspection Process | 8.2 Visual Inspection-The inspector(s) shall visually verify characteristics of PV Module as per the Visual Inspection Criteria | As per the bidder inspection criteria. | Technical | Visual Inspection Criteria shall be agreed with the Supplier prior to Pre-dispatch Inspection
70 | SOS &TS | 11 of 18 - 217 | PART – C: PRE-DISPATCH INSPECTION PROTOCOL 8 Inspection Process | 8.3 Electroluminescence (EL) Inspection- The inspector(s) shall visually verify characteristics of PV Module as per the Visual Inspection Criteria | As per the bidder EL inspection Criteria. | Technical | Electroluminescence Criteria shall be agreed with the Supplier prior to Pre-dispatch Inspection
71 | SoS & TS | 5 of 18 - 217 | PART – B: TECHNICAL SPECIFICATIONS - 2 Standards | The PV Module shall be enlisted in ALMM – List I in accordance with extant provisions of Approved Models and Manufacturers of Solar Photovoltaic Modules (Requirements for Compulsory Registration, Order, 2019) and subsequent amendments | Please confirm module under ALMM prior to invoice is acceptable | Technical | Extant provisions of the Approved Models and Manufacturers of Solar Photovoltaic Modules (Requirements for Compulsory Registration, Order, 2019) and subsequent amendments shall govern the acceptability.
72 |  |  |  | Minimum and maximum Wp of module | Please clarify if there is any minimum or maximum Wp of modules required. | Technical | As stated clearly in the tender document, it should be greater than or equal to 540 Wp.
73 |  |  |  | Cell/ Module Technology | Please confirm module can be monofacial or bifacial or only Bifacial modules as | Technical | It can be either monofacial or bifacial.
74 |  |  |  | 1 Flash Test - General inspection level I | Please Accept Special Inspection Level S4 | Technical | Please refer S. No. 5 of Amendment
75 |  |  |  | 2 Visual Inspection - General inspection level I | Please Accept Special Inspection Level S4 | Technical | Please refer S. No. 5 of Amendment
76 |  |  |  | 3 Electroluminescence - General inspection level I | Please Accept Special Inspection Level S4 | Technical | Please refer S. No. 5 of Amendment
77 |  |  |  | 4 Electrical Characteristics - Special inspection level S-2 | Please Accept Special Inspection Level S4 | Technical | The terms and conditions of the tender document shall prevail.
78 |  |  |  | De-loading factor for higher module | Is there any Evaluation / deloading factor for higher Wp module Supply | Technical | No, there is no deloading factor for higher Wp supply.
79 |  |  |  | Price variation | Please include Price variation | Contractual | The terms and conditions of the tender document shall prevail.
80 |  | 128 |  | The Time for Completion for the entire 400 MWp (DC) Solar PV Module Package in total shall be 9 (Nine) Months from the Date of the Contract Agreement / Purchase & Service Order | Please clarify it is from Purchase order or Contract Agreement (28 days) | Contractual | The Zero Date will be signing of Contract Agreement (herein also refer as Purchase/ Service Order)
81 | SoS & TS | 213 | 5.2 | PV Modules shall be warranted for power output, as specified by the bidder in the Degradation Curve, for a minimum period of 25 years commencing from the date of the last Tax invoice raised under the contract. | Should be valid from respective module invoice and not from the last module invoice | Technical | The terms and conditions of the tender document shall prevail.
82 | SoS & TS | 213 | 5.5 | This insurance should be valid for a period of 25 years from the date of last Tax Invoice under the contract and the claim period should extend for a minimum of 1 year beyond this date. Warranty | Should be valid from respective module invoice and not from the last module invoice | Technical | The terms and conditions of the tender document shall prevail.
83 | SoS & TS | 208 | 1.4 | The Bidder shall offer only one type of PV Module with same Dimensions as per the specifications provided herein. The PV Module dimensions shall not change from the Guaranteed Technical Particular Datasheet (Form: T-01) provided with the bid. | Request SECI to kindly provide the Guaranteed Technical Particular Datasheet (Form: T-01) format as it is not the part of tender document. | Technical | Please Refer S. No. 6 of Amendment.
84 | SoS & TS | 208/226 | 1.1 | The scope of supply includes Manufacturing, Testing, Packing and Forwarding, Transportation to Site and Unloading of domestically manufactured Solar PV Modules with domestically manufactured solar cells | 1. For MonoPERC - bifacial & Monofacial- We have Certified with DCR and Non -DCR cell | Technical | As per the specifications, both Cells and Modules shall be domestically manufactured.
85 | SoS & TS | 208/226 | 1.5 | The Supplier shall submit PAN file of the PV Modules to be supplied (certified by an ILAC member signatory accredited laboratory) within 60 days from the date of Award. | We request SECI to kindly confirm one Wattage PAN file from Bin distribution is enough. | Technical | Supplier shall submit one PAN File for each nameplate Power rating of PV Modules supplied under the Contract. For e.g., If 2 Module ratings of 540 Wp and 545 Wp are proposed, PAN files of each rating shall be submitted.
86 | SoS & TS | 210/226 | 2.1 |  | 1. In BIS Portal the below TRF is only applicable to raise request with 2010 Version, IS 14286: 2010 First Revision Request SECI to kindly consider to consider the same. | Technical | The terms and conditions of the tender document shall prevail. Compliance to equivalent IEC standards is acceptable.
87 | SoS & TS | 212/226 | 4.3 |  | 1. For TOPCon Glass to Glass module, Consider EPE- EPE /EPE - EVA on both front and backsides as this is widely used in market as there are slippage issues of POE during manufacturing and changing BoM will need to do additional certification. 2. For MonoPERC modules , please confirm can we use EVA EPE Combination or only EVA combination is allowed we request you to kindly keep it open. | Technical | Please refer S. No. 1 of Amendment
88 | SoS & TS | 212/226 | 4.7 | iii) Type of cell (xi) Other relevant information on traceability of solar cells and modules as per ISO 9000 series. | iii) Request SECI to kindly remove Type of cell in RFID Requirement as adding the detail in RFID might be technically challenging. Cell datasheet and manufacturing details can be shared with the SECI team before dispatch of first lot. (xi) Request you to kindly clarify what exact information is required. | Technical | Accepted, Please refer S.No. 2 of Amendment
89 | SoS & TS | 214/226 | 7.3 | Current binning of modules shall be employed so that current mismatch of modules in a pallet does not exceed 150 mA at Maximum Power (Imp). Different colour codes shall be provided on the modules as well as pallet for identification of different bins. The Supplier shall submit the binning scheme to the Employer for approval, prior to manufacturing. | Request SECI to kindly consider Wattage binning without colour coding which is widely used in market it will also reduce the number of Bins compared current binning | Technical | The terms and conditions of the tender document shall prevail.
90 | SoS & TS | 217/226 | 6 | The inspector(s) shall commence inspection process by randomly selecting samples from the list of module serial numbers (pallet-wise) provided by Supplier. Number of samples shall be chosen as per the inspection level mentioned in the table below and ISO 2859-1 (Single Sampling Plan for Normal Inspection). However, the inspector(s) shall reserve the right to switch to tightened or reduced level of Inspection as per the lot quality. Extracts of ISO 2859-1 relevant for determination of sample size are attached in Annexure-1. | We request SECI that the decision of providing the inspection level either to be normal or reduced can be decided by the inspector and not the tightened inspection will be followed for it. Tightened inspection will be followed incase of any re-sampling or re-inspection. As per ISO Tightened inspection is invoked when the inspection results of a predetermined number of consecutive lots indicate that the process average might be poorer than the AQL(acceptance quality limit) | Technical | Please refer S. No. 5 of Amendment
91 | SPC | 128/226 | 3 | However, it is preferred that the Module deliveries are made starting October 2025 till Jan 2026, with the completion of entire deliveries by Jan 2026. | Request SECI to kindly clarify if this preferred delivery schedule is the final schedule as the supply window is of 9 month and preferred delivery is in 4 months only. will there be any delivery required before Oct'25, kindly clarify. | Contractual | The delivery period of modules as mentioned in the SPC Section of the tender document shall remain firm. However, depending on cases, relaxation may be provided to start the delivery of modules before October 2025.
92 | SoS & TS | 208/226 | 1.1 | Unloading of the consignment (i.e. PV Modules supplied under this Contract) shall be the responsibility of the Employer. However, the Supplier shall depute an authorized representative to the site commencing from the date of delivery of first consignment till the completion of all Supplies under this Contract for verification of receipt of the consignment in good condition, and to facilitate the handing over of the same to the Employer/Employer's assignee. Any physical damages identified during the process shall be jointly documented in a measurement sheet. The Supplier shall replace the damaged/defective modules as per the terms of the Contract. | We request SECI to kindly follow the below process to report any damaged modules without deploying any personal from supplier: Any damage to modules during transit shall be reported within 48 Hrs days of delivery with following docs: • Photos of pallets inside the vehicle before unloading and video of opening of pallets which are suspected to have damages or found in deformed/tilted condition. • Damage remarks on transporter's LR copy duly signed and stamped with serial numbers of PV modules. | Contractual | The terms and conditions of the tender document shall prevail.
93 | SoS & TS | 211/226 | 3 | Power Rating at STC ≥ 540 Wp | Request SECI to kindly clarify if we can supply 78 full cell (156 Half cut cell) modules to achieve higher power class module ≥ 540 Wp. | Technical | PV Modules with rating >= 540 Wp shall be acceptable. The terms and conditions of the tender document shall prevail.
94 | SPC | 134/226 | 13 | Interest bearing advance of 10% of the total value of Supply portion shall be released to supplier against Submission of Test Certificates / Manufacturing Clearance, detailed Performa invoice of contractor and against submission of unconditional & irrevocable Advance Bank Guarantee (ABG) with a validity period up to date of final supply amounting to 110% of total advance amount. The ABG needs to be submitted in addition to the Contract Performance Security. | 1. We request SECI to kindly provide 10% advance without any interest. 2. Request you to kindly accept the ABG equal to 100% advance amount | Contractual | The terms and conditions of the tender document shall prevail.
95 | BDS | 72/226 | 6 | The bid validity period shall be 180 (One Hundred and Eighty Days) from the date of opening of Techno-Commercial Bid (Envelope-I). | Considering the volatility of the market we request SECI to kindly make the bid validity period to 60 Days | Contractual | The terms and conditions of the tender document shall prevail.
96 | SPC | 134/226 | B | For Freight and Testing Services Portion, 100% of the payment shall be paid after successful delivery and acceptance of materials at site. | We request SECI to kindly make the payment for freight also on prorata basis similar to the modules. | Contractual | The terms and conditions of the tender document shall prevail.
97 | IFB | 16/226 | J | CONTRACT PERFORMANCE SECURITY 10% of the Total Project/Order Cost for a total period of 24 months. | We request SECI as total contract period is of ~12 Months request you to kindly consider CPS for 12-14 months | Contractual | The terms and conditions of the tender document shall prevail.
98 | Annex To BDS | 78/226 | 1.3.1 | Bidders may use the technical and financial credentials of their Parent, Holding, Subsidiary, Affiliate for qualifying the above mentioned technical and financial qualification requirements as per clause 1.3. | There in no clause 1.3 in the Annexure to BDS, Request you to kindly clarify. | Contractual | This is a typo. The clause itself is self explanatory which means participation suppliers may use the technical and financial credentials of their Parent, Holding, Subsidiary, Affiliate for qualifying the technical and financial qualification requirements.
99 |  |  |  | General | If Manufacturer is using parent company financial credential for qualifying in the tender then there is not need of manufacturer to fulfil any of the financial criteria on its own, kindly clarify. | Contractual | The clause itself is self explanatory which means participation suppliers may use the technical and financial credentials of their Parent, Holding, Subsidiary, Affiliate for qualifying the technical and financial qualification requirements.

## Amendment 01
Sl. No. | Tender Section | Page No. | Clause No | Original Version | Amendment
1 | Section VII Scope of Supply and Technical Specifications (PART – B: TECHNICAL SPECIFICATIONS) | SoS & TS Page 7 of 19 | 4.7 | Each PV Module shall be provided with a RFID tag which is embedded inside the module lamination and must be able to withstand harsh environmental conditions. The RFID data base shall contain the following information. RFID scanner and database of all the modules containing the following information shall also be provided. (i) Name of the Manufacturer of PV Module (ii) Name of the Manufacturer of Solar cells (iii) Type of cell (iv) Month and year of the manufacture (separately for solar cells and module) (v) Country of origin (separately for solar cells and module) (vi) I-V curve for the module (vii) Peak Wattage, Im, Vm and FF for the module (viii) Unique Serial No. and Model No. of the module. (ix) Date and year of obtaining IEC PV module qualification certificate (x) Name of the test lab issuing IEC certificate (xi) Other relevant information on traceability of solar cells and modules as per ISO 9000 series. | The following information must be mentioned in the RFID used on each module (This can be inside or outside the laminate, but must be able to withstand harsh environmental conditions): i. Name of the manufacturer of PV Module ii. Name of the Manufacturer of Solar cells iii. Month and year of the manufacture (separately for solar cells and module) iv. Country of origin (separately for solar cells and module) v. I-V curve for the module at Standard Test Condition (1000 W/m 2, AM 1.5, 25 DegreeCelcius) vi. Wattage, Im, Vm and FF for the module vii. Unique Serial No. and Model No. of the module viii. Date and year of obtaining IEC PV module qualification certificate ix. Name of the test lab issuing IEC certificate x. Other relevant information on traceability of solar cells and module as per ISO 9000 Supplier shall also provide soft copy of above parametric data for each module.
2 | Section VII Scope of Supply and Technical Specifications (PART – B: TECHNICAL SPECIFICATIONS) | SoS & TS Page 7 of 19 | 4.3 | Encapsulant Type For TOPCon Modules: (i) Glass/backsheet Modules - POE or EPE on both front and back sides of the cell (ii) Glass/Glass Modules – POE on Front side For Mono PERC Modules - EVA | Encapsulant Type for TOPCon Modules: (i) Glass/backsheet Modules - POE/EPE on both front and back sides of the cell (ii) Glass/Glass Modules – POE/EPE on Front side, EVA/POE/EPE on Rear side For Mono PERC Bifacial Modules: (i) Glass/backsheet Modules : POE/EPE on rear side, EVA/EPE on Front side (ii) Glass/Glass Modules: EVA/EPE on front side, EVA/EPE on rear side For Mono PERC Monofacial Modules: EVA/EPE on rear side, EVA/EPE on Front side
3 | SECTION - VII PART – B: TECHNICAL SPECIFICATIONS | SoS & TS Page 9 of 19 | 7.4 | The Manufacturing shall start only after the clearance by the Owner after the material inspection. | Manufacturing will start as per the mutually agreed schedule of the production between supplier & Owner.
4 | Section VII Scope of Supply and Technical Specifications (PART – B: TECHNICAL SPECIFICATIONS) | SoS & TS Page 9 of 19 | 7.6 | The Owner shall perform material inspection at the Manufacturer’s factory before the start of proposed manufacturing schedule. Proof of procurement of components as per the approved BOM mentioning manufacturer name, manufacturing date and relevant test certificate shall be submitted during material inspection for verification. | The Owner shall perform material inspection at the Manufacturer’s factory during manufacturing of Modules or during pre-dispatch Inspection. Proof of procurement of components as per the approved BOM mentioning manufacturer name, manufacturing date and relevant test certificate shall be submitted during material inspection for verification.
5 | SoS & TS | 217/226 | 6 | The inspector(s) shall commence inspection process by randomly selecting samples from the list of module serial numbers (pallet-wise) provided by Supplier. Number of samples shall be chosen as per the inspection level mentioned in the table below and ISO 2859-1 (Single Sampling Plan for Normal Inspection). However, the inspector(s) shall reserve the right to switch to tightened or reduced level of Inspection as per the lot quality. Extracts of ISO 2859-1 relevant for determination of sample size are attached in Annexure-1. | The inspector(s) shall commence inspection process by randomly selecting samples from the list of module serial numbers (pallet-wise) provided by Supplier. Number of samples shall be chosen as per the inspection level mentioned in the table below and ISO 2859-1 (Single Sampling Plan for Normal Inspection). However, the inspector(s) shall reserve the right to switch to tightened or reduced level of Inspection as per the lot quality. Extracts of ISO 2859-1 relevant for determination of sample size are attached in Annexure-1.
6 | Technical Forms - T-01 and T-02 | - | - | - | Format T-01 (Guarantee Technical Particular Datasheet) and T-02 (Degradation Curve of PV Module) enclosed with the Pre Bid Clarification and Amendment 01 sheet.
7 | Section VII Scope of Supply and Technical Specifications (PART – A: SCOPE OF SUPPLY) | 3 of 19 | 1.1 | The scope of supply includes Manufacturing, Testing, Packing and Forwarding, Transportation to Site and Unloading of domestically manufactured Solar PV Modules with domestically manufactured solar cells. | The scope of supply includes Manufacturing, Testing, Packing, Forwarding and Transportation to Site of domestically manufactured Solar PV Modules with domestically manufactured solar cells.
8 | Section VII Scope of Supply and Technical Specifications (PART – A: SCOPE OF SUPPLY) | 3 of 19 | 1.3 | The Owner reserves the right to increase or decrease the quoted PV Module capacity by ± 10% at the time of placing of the order on the same price, terms and conditions of the contract. The Owner also reserves the right to order up to additional 5% of awarded PV Module capacity on the same price, terms and conditions of the contract, during the currency of the contract by giving suitable extension in delivery period for the additional quantity. | The Owner reserves the right to increase or decrease the quoted PV Module capacity by ± 10% at the time of placing of the order on the same price, terms and conditions of the contract. The Owner reserves the right to place a repeat order up to an additional quantity of 100% (Hundred percentage) of the respective awarded PV Module package capacity on the same price, terms, and conditions of the original contract, by providing suitable extension in delivery period for the additional repeat order quantity. The provision of such additional requirement of supply up to 100% on repeat order basis will be done on mutual agreement basis & the award of such repeated order will be done maximum within 06 months of the original awarded capacity.
9 | Section VII Scope of Supply and Technical Specifications (PART – A: SCOPE OF SUPPLY) | 3 of 19 | 1.5 | The Supplier shall submit PAN file of the PV Modules to be supplied (certified by an ILAC member signatory accredited laboratory) within 60 days from the date of Award. | The Supplier shall submit PAN file of the PV Modules to be supplied (certified by an ILAC member signatory accredited laboratory) within 20 days from the date of Award.
10 | Section VII Scope of Supply and Technical Specifications (PART – A: SCOPE OF SUPPLY) | 4 of 19 | 1.7 | Note: The Owner shall intimate a Notice to Proceed (NTP) to the Supplier for commencement of supply at least 60 days prior to the first delivery date. | Note: The Owner shall intimate a Notice to Proceed (NTP) to the Supplier for commencement of supply at least 30 days prior to the first delivery date.
11 | Section V Special Purchase Conditions | 4 of 9 | 6 | b) In case the supplier is unable to submit GTP Datasheet, Drawing & Test Certificates within the specified deadline of 03 months from the issuance of Contract Agreement / Purchase & Service Order. | b) In case the supplier is unable to submit GTP Datasheet, Drawing & Test Certificates within the specified deadline of 10 days from the issuance of Contract Agreement / Purchase & Service Order.