## Compiled Pre Bid Queries
Tender for Design, Engineering, Procurement & Supply, Construction & Erection, Testing, Commissioning and Comprehensive Operation & Maintenance (O&M) for 10 (ten) years of SCCL’s 10 MW FSPV project at STPP, Telangana, India
Tender No : SECI/C&P/PMC/11/05/2024-25
Sl. No. | Tender Section | Page No. | Clause No | Description as per Tender Document | Queries | Category (Finance/Technical/Contractual) | Clarifications
1 |  | 356 | Clause 2.0 | CMCS, INVERTER ROOMS, SECURITY ROOM & STORE ROOM | Bidder is requesting to provide KMZ file (or) DWG file of Floating area & other locations like CMCS,Inverter rooms, Security room, Store room & Switchyard area. | Technical | kml file attached with the Pre Bid Clarification and Amendment 01 sheet.
2 | SECTION - VII SUB-SECTION C | 88 | SECTION - VII SUB-SECTION C | 5 Geotechnical Investigations (On-Shore) - For the on-shore investigation, there shall be minimum 2 nos. of Boreholes per patch of land, 1 no. of Trial pit, 2 nos. of ERT, 2 nos. of CBR and 1 no. of Ground water sample for laboratory investigations. | Bidder request to confirm how much area have to be considered per Patch of land | Technical | The contractor has to use the corresponding report provided under SA-C3 at their own risk and cost. SCCL/SECI will not be held responsible for any changes in soil strata or any issues arising during construction due to the reliance on the existing geotechnical report
3 | SECTION - VII SUB-SECTION A | 17 | SECTION - VII SUB-SECTION A | 7 Civil Works - 7.5 Construction of Portable Storage Cabin /PEB of area sufficient enough to store spares. | Bidder request to provide the Storage Cabin area | Technical | Terms and conditions of tender document shall prevail.
4 | SUB-SECTION D GENERAL ANNEXURE E | 157 | SUB-SECTION D GENERAL ANNEXURE E | Plant Boundary Fencing (if applicable) & Gate (Also refer S.No. 3 for Steel works as applicable) | Bidder request to confirm whether Plant boundary fencing will be applicable only for the offshore area or it has to be considered for the overall reservoir area | Technical | Requirements of fencing are applicable only for on-shore installations.
5 | SECTION - VII SUB-SECTION C | 102 | SECTION - VII SUB-SECTION C | 26 Water Supply and Cleaning of Modules | Bidder request to confirm module cleaning system as Wet cleaning system | Technical | Requirement of wet cleaning system has been specified in Cl. 26 of SS-C: Technical Specifications-Civil of the tender.
6 | SUB-SECTION - D GENERAL ANNEXURE I | 202 | 3.1.2 | Soiling losses shall not be accounted for in the assessment of Results. Therefore, adequate Module cleaning exercise shall be undertaken prior to commencement of Commissioning process | Bidder need clarification on this with out considering the soil losses unable to give the generation analysis, please suggest the value which we need to consider | Technical | No correction in generation shall be made due to soiling losses during commissioning.
7 | SECTION - VII SUB-SECTION F |  | 1.C | Module degradation factor will not be considered for first year CUF calculation. It is the Contactor’s responsibility to envisage and install extra DC capacity to accommodate any degradation during first year. | Bidder requesting modification on this point, Vendor it self mentioned the 2 % degradation in first year, with out considering the degradation generation commitment is not possible | Technical | Terms and conditions of tender document shall prevail.
8 |  |  |  |  | Is there any requirement for Harmonic Filters? | Technical | Contractor shall install harmonics filters in order to meet the requirements as per CEA Technical Standards for connectivity to the Grid. if required
9 |  |  |  |  | There is any limitation up to inverter line loss. | Technical | Kindly refer to Cl. 6.5 for acceptable voltage drop limits in the AC cable run between PCU (inverter) and IDT. Further, contractor may limit the losses to meet operational acceptance requirement as mentioned in the NIT.
10 |  |  |  |  | Bidder required Minimum DC losses Consideration Details as per the SECI | Technical | 1.5% DC losses as per Cl. No. 3.6 (ii) SS-B Technical Specifications - Electrical
11 | SECTION - VII SUB-SECTION B | 34 | 4.3.5 | Inverter Transformer shall have shield winding between LV & HV windings. Each LV winding must be capable of handling non-sinusoidal voltage with voltage gradient as specified by the inverter manufacturer. | Bidder need conformation on which winding material we need to consider aluminium/ Copper | Technical | Bidder has to use Copper only for meeting other specification given in Cl. 4 of SS-B Technical Specifications - Electrical.
12 |  |  |  |  | Bidder required clarification on SCADA Need to consider separate for both plants? | Technical | There may be one set of SCADA hardware, but it must maintain separate data for each plant since the metering for each plant is different and separate communication is to be maintained with the SLDC for each 5 MW project.
13 | - | - | - | - | With the reference of above name of work, please provide BID SURETY format. | Contractual | Kindly refer to Annexure I to Pre Bid Clarification and Amendment 01.
14 | NIT | 78 | 1.2 | The bidder should have experience in EPC execution / Developer of Ground mounted Solar PV Projects on Turnkey basis including Design, Supply (Supply of Modules/Inverters can be inclusive or exclusive in the bidder’s scope in the past experience), Installation and Commissioning of Grid connected Solar PV Power Plant of cumulative Capacity not less than 5 (Five) MW in last seven years as on last date of bid submission. However, such Grid connected Solar PV Power Plant capacity must have been in satisfactory operation for at least six (06) months prior to the last date of bid submission. | We have already executed a 7.324 MWp Floating Solar Power which is operational since more than a year and hope we are eligible considering this. In addition to this we have executed a 23 MWp Roof Top project with 8.66 MWp connected at 33 kV which is also operational. Kindly clarify. | Contractual | The terms and conditions of the tender document shall prevail. Experience of either Floating or Ground Mounted or both ground and floating solar PV projects will be considered for qualifying the Technical Eligibility Conditions.
15 |  |  |  |  | Request you to kindly share the GTP & GA drawings of the previously proposed Transformer. | Technical | GTP of the auxiliary transformer is provided at SA-D.GA drawing & other relevant documents shall be shared to successful bidder.
16 |  |  |  |  | Request you to kindly extend the bid date | Contractual | Extension will be duly reflected on SECI's website and ETS Portal.
17 |  |  |  |  | Please share the Dimensions& weight of the Dead weight anchor blocks | Technical | Kindly refer to SA-F for all the required details.
18 | Project Particulars | 7 | 1 | Metering Point: 1. 5MW Grid End metering at PAVNOOR S/S 2. 5MW Grid End metering at KUNDARAM S/S | As Bidder standing only one ABT meter is required at PAVNOOR substation end and one ABT meter is required at KUNDARAM substation end | Technical | ABT meters (Main, Check and standby) with all necessary metering rated CTs and PTs at the Metering Point as per CEA Metering Regulations 2006 as amended time to time and state metering code namely TSERC's regulations.
19 | Design and Engineering | 11 | 3.4 | Bathymetric Survey (Specific Annexure – C1) | Kindly share the dwg file of Bathymetric Survey | Technical | DWG file not available. Bidder to review the provided bathymetric report only.
20 | Design and Engineering | 11 | 3.4 | Topography Survey of Land & Reservoir (Specific Annexure – C2) | Kindly share the dwg file of Topography Survey of Land & Reservoir | Technical | DWG file not available. Bidder to review the provided topographic survey report only.
21 | Procurement & Supply | 13 | 4.7 | Power Conditioning Units (PCU) | Kindly share the OND file of central inverter, Installation Manual, other relative documents and vendor contact details. Central inverter is free issue by client then Warrantee of central inverter during the O&M period is in client scope explain it? | Technical | 1. Make of Central Inverter: TMEIC Model of Central Inverter: PVU L0920ER However, obtaining the OND file (of model mentioned above) from OEM for the purpose of bidding shall be responsibility of the bidder. 2. Installation manual & other relative documents shall be shared to successful bidder. 3. Contractor shall be responsible for servicing of the warranty during O&M period. Kindly refer to Cl. 4.35 of SS-A: Scope of Works of Technical Specifications for more details.
22 | Procurement & Supply | 14 | 4.7 | 1 No. of 63 KVA auxiliary transformer is provided by Owner (SCCL) at site and shall be used by contractor for the Plant design. | Kindly share the Installation Manual and other relative document. Auxiliary transformer is free issue by client then Warrantee of auxiliary transformer during the O&M period is in client scope explain it? | Technical | 1. Installation manual & other relative documents shall be shared to successful bidder. 2. Contractor shall be responsible for servicing of the warranty during O&M period. Kindly refer to Cl. 4.35 of SS-A: Scope of Works of Technical Specifications for more details.
23 | Solar and DC Cables | 30 | 3.2 | Both solar and DC cables shall be marine grade cables complying with relevant standards. | Kindly specified the marine grade and relevant standards. | Technical | VOID. Refer to Amendment-1 Sl. No. 1
24 | Solar and DC Cables | 30 | 3.6 (ii) | In case of central inverters, average voltage drop in the cables (from PV Modules to PCU) shall be limited to 1.5 % of the rated voltage. | To maintain CUF 22.8% we can consider DC loss 2% from PV module to PCU in case of central inverter. | Technical | Terms and conditions of tender document shall prevail.
25 | Installation | 31 | 3.9.7 | Solar cables or group of solar cables combined through branch connector may be laid over ground on GI or FRP cable trays / underground through Double Wall Corrugated (DWC) HDPE conduits from PV String (Series connection of PV Modules) to SCB/String Inverter. The size of the conduit or pipe shall be selected on the basis of 40% fill criteria. Solar cable terminations shall be made with connectors complying IS 16781 / IEC 62852. The connectors shall have degree of protection of IP 68. | Kindly clarify the cable laid from SCB to Inverter is in ladder type GI tray or any other. | Technical | For cables routed onshore, Clause No. 3.9.7 may be referred. For cables routed offshore, Contractor shall place the cables on floats with suitable arrangements to secure them against submersion in water. Please refer amendment-1 Sl. No. 2.
26 | Circuit Breakers | 40 | 5.4.3 | The rated control voltage shall be 110 VDC/220 VDC | Kindly confirm the rated control voltage is 110V DC or 220V DC. | Technical | Terms and conditions of tender document shall prevail.
27 | Annual CUF Guarantee | 264 | 1 (C) | Reference Irradiation for the site = 1918.4 kWh/m2/year | kindly share the per month solar Irradiation value at site. | Technical | Terms and conditions of tender document shall prevail.
28 |  |  |  |  | Kindly share the preliminary SLD. | Technical | Central inverters will be provided by SCCL. SLD shall be in the scope of bidder.
29 |  |  |  |  | Kindly share the reservoir cross section drawing (Civil). | Technical | PDf of sectional drawing of reservoir attached as Annexure to the Pre Bid Clarification and Amendment 01
30 | Technical QUALIFYING REQUIREMENTS (QR) | 78 of 244 | 1.2 | IB. The bidder should have experience in EPC execution of Ground mounted Solar Projects on Turnkey basis including Design, supply (Supply of Modules/Inverters can be inclusive or exclusive in the bidder’s scope in the past experience), installation & commissioning of at least 02 (Two) Grid connected Solar PV Power Plant Projects having an individual capacity of 01 (One) MW or above in last seven years as on last date of bid submission. However, such Grid connected Solar PV Power Plant capacity must have been in satisfactory operation for at least six (06) months prior to the last date of bid submission. | IB. The bidder should have experience in EPC execution of Ground mounted Solar Projects on Turnkey basis including Design, supply (Supply of Modules/Inverters can be inclusive or exclusive in the bidder’s scope in the past experience), installation & commissioning of at least 02 (Two) Grid connected Solar PV Power Plant Projects having an individual capacity of 01 (One) MW or above OR 01 (One) Grid connected Solar PV Power Plant Projects having a capacity of 05 (Five) MW Minimum in last seven years as on last date of bid submission. However, such Grid connected Solar PV Power Plant capacity must have been in satisfactory operation for at least six (06) months prior to the last date of bid submission. | Contractual | The terms and conditions of the tender document shall prevail. Experience of either Floating or Ground Mounted or both ground and floating solar PV projects will be considered for qualifying the Technical Eligibility Conditions.
31 | Annexure to Bid Data Sheet (QUALIFYING REQUIREMENTS ) | 77 | 1.1 | The bidder should be an Indian company registered in India | Enclosed Copy of Registration, Please Confirm eligibility for Participation | Contractual | The terms and conditions of the tender document shall prevail.
32 | Sub-Section A: SOW | 14 | 7.6 | Construction and installation of any additional anchor blocks, if required, shall be in the scope of contractor. Reports of NDT for the existing anchor blocks shall be shared by the Owner prior to submission of bids. | We request you to kindly share us the NDT details of existing blocks | Technical | Kindly refer Amendment - 1 Sl. No. 3
33 | Sub-Section A: SOW | 15 | 7.9 | Construction of IDT Foundation and associated works Note: IDT Foundation drawing have been provided under ‘Specific Annexure – I’. This foundation has already been constructed at the site. The contractor may use the same for the installation of IDT if the mounting location and structural requirements are met. Alternatively, the contractor shall construct the foundation based on the IDT requirement. | As we have to install 2 nos IDT, the existing IDT wont be suitable, Kindly confirm whether we have to demolish and construct as per the number of transformers. | Technical | Existing IDT foundation was planned for 2 nos. of 5MVA transformers. Kindly refer Cl. 7.9 of SS-A: Scope of Works for further details.
34 | TS Page 13 of 32 | 13 | 9 | Peripheral boundary Wall / Fence & Main Gate | In tender it is mentioned as Void but during the pre bid me, it was informed that we have to fence the whole area as well as the existing plant. Hence request you to confirm the scope. | Technical | As per CEA & TSERC all the electrical equipment yards like IDT yard & switchyards at Plant End & grid end bay shall be fenced. Moreover the peripheral boundary wall (Pre cast compound wall )around the plant is under the scope of EPC only.
35 | TS Page 22 of 32 | 22 | 26 | Water used for drinking & PV module cleaning purpose shall be of potable quality and fit for cleaning the modules with TDS generally not more than 75 PPM. In case of higher salt contents, the water shall be thoroughly squeezed off to prevent salt deposition over module surface. However, water with TDS more than 200 PPM shall not be used directly for module cleaning without suitable treatment to control the TDS within acceptable limits. The water must be free from any grit and any physical contaminants that could damage the panel surface. | Kindly confirm the water will be provided by the SCCL or EPC contractor has to arrange.& kindly confirm whether the RO plant is required or Not. | Technical | Arranging water shall be in the scope of the EPC contractor. Sufficient capacity of RO plant for cleaning of PV modules and other purposes shall be installed mandatorily
36 | ANNEXURE-2 | 40 | 1 | The Contractor guarantees the annual CUF committed herein over the O&M Period (“Annual CUF Guarantee”). In the event the CUF is less than the Guaranteed CUF, the Contractor shall immediately, upon demand, indemnify the Owner, as liquidated damages and not as penalty, amounts equivalent to remuneration of the equivalent shortfall Energy, subject to a maximum of hundred (100%) percent of the Total Annual O&M Price. | The Guaranteed CUF of 22.8% is for through out the O&M period or it is for first year alone | Technical | CUF guarantee is required for the entire O&M Period
37 | Sub-Section SA-D: Equipment to be Supplied by Owner | 2 | 1.2 | Datasheet of Power Conditioning Unit (840kW) | The inverters are pre supplied for this Project & if there is any Operational issues or damage to the PCU components, it will have adverse effect on the system & generation, hence we request you to consider and let the L1 bidder supply the inverter as per their design. As EPC contractor cannot be held liable for any operational issues of the Owner supplied material. | Technical | Terms and conditions of tender document shall prevail.
38 | BDS Page 3 of 13 | 3 | 7 | EMD (ITB 16) Further the EMD will also be accepted in the form of Insurance Surety Bond as per Format 16 of the tender document. | Format 16 in the tender document. Is missing, hence request you to kindly provide the same | Contractual | Kindly refer to Annexure I to Pre Bid Clarification and Amendment 01.
39 | SCC Page 3 of 13 | 3 |  | Date of successful commissioning (D + 06 Months) | As there is multiple works involved along with the ROW & TL of 23 Kms line, hence we request you to kindly provide some additional time limit. As currently there is an shortage of DCR modules in India, hence we request you to consider unforeseen delays if due to shortage of modules and Disscomm approvals. | Technical | Terms and conditions of tender document shall prevail.
40 |  |  |  |  | The Transformer at Pavnoor Substation is to be upgraded by Disscomm from existing 3.15 MW to 5 MWA, hence kindly clarify whether upgradation will be in Discomm scope and cost or EPC contractor has to bear the cost | Technical | The same will be in DISCOM scope only. However the EPC contractor has to bear the cost.

## Amendment-1
Tender No. SECI/C&P/PMC/11/05/2024-25
The Design, Engineering, Supply, Construction, Erection, Testing & Commissioning of 10 MW (AC) Floating Solar PV Project having 10 years plant O&M
S. No. | Section | Page No. | Clause | Original Version | Amendment
1 | SS-B:TS-Electrical | 10 | 3.2 | Both solar and DC cables shall be marine grade cables complying with relevant standards. | VOID
2 | SS-B:TS-Electrical | 11 | 3.9.6 | Solar/DC cables shall be laid on the waterbed from PV Modules/SCB to inverter, if placed on shore. There shall be one spare run of cable per inverter. | Solar/DC cables from PV modules/SCBs to the inverter, if placed onshore, shall be securely laid on floats with appropriate arrangements to prevent submersion in water. There shall be one spare run of cable per inverter.
3 | Sub-Section A: SOW | 14 | 7.6 | Construction and installation of any additional anchor blocks, if required, shall be in the scope of contractor. Reports of NDT for the existing anchor blocks shall be shared by the Owner prior to submission of bids. | The successful bidder shall carry out NDT test for existing anchor blocks in reservoir and submit the certificate to the PMC&Owner for final approval. If strength is found weakreplaacement/repair of anchor block shall be under the scope of contractor.
4 | Special Conditions of Contract | 6 of 13 | 9 (Liquidated Damages (GCC Clause 20)) | 20.1 Subject to Force Majeure Clause, if the contractor fails to comply with the timelines for completion, the application of LD will be as follows: 20.1.1 For delay in synchronization & commissioning: INR 20,000/MW/day for the capacity not commissioned. On this account the maximum applicable LD is 3% of total contract price. 20.1.2. For delay in operation acceptance: INR 20,000/MW/day for total capacity. On this account the maximum applicable LD is 1.5% of total contract price. 20.1.3 For delay in final acceptance: The contractor shall pay to the owner a sum equivalent to half percent (0.5%) per week of the contract price (supply and service) for the balance activities as LD for such default and not as a penalty, without prejudice to the owner’s other remedies under the contract, if final acceptance is not obtained within 12 months form operational acceptance. On this account the maximum applicable LD is 0.5% of total contract price. 20.2 The Owner may, without prejudice to any other method of recovery, deduct the amount of such damages from any amount due or to become due to the Contractor. The payment or deduction of such damages shall not relieve the Contractor from his obligation to complete the Works, or from any other of his obligations and liabilities under the Contract. Once the maximum limit is reached, Owner may consider the termination of contract and/or shall have the discretion of getting executed the work from the Contractor with the maximum limit of Liquidated damages. Any such recovery on account of the Liquidated damages can be done from the running bills of the Contractor by Owner. 20.3 The Owner shall at its sole discretion upon reaching the maximum LD limit , as an alternative to the Liquidated Damages at its option, get work executed from elsewhere at the risk and cost of the Contractor irrespective of the fact whether the scope of Contract is identical to the original scope of Contract and in case the Owner chooses the alternative course as mentioned, it will be entitled to recover compensation/ damages from the Contractor irrespective of maximum limit prescribed under Clause 20.1. 20.4 The Owner may by giving (01) one-month notice to the Contractor cancel the Contract without prejudice to the Owner’s right under Clauses 20.1,20.2 and 20.3 or any other provisions contained in the Contract to determine the Contract and claim damages from the Contractor. 20.5 No bonus will be given for earlier Commissioning of the Facilities or part thereof. | 20.1 Subject to Force Majeure Clause, if the contractor fails to comply with the timelines for completion, the application of LD will be as follows: 20.1.1 For delay in synchronization & commissioning: INR 20,000/MW/day for the capacity not commissioned. On this account the maximum applicable LD is 5% of total contract price. 20.2 The Owner may, without prejudice to any other method of recovery, deduct the amount of such damages from any amount due or to become due to the Contractor. The payment or deduction of such damages shall not relieve the Contractor from his obligation to complete the Works, or from any other of his obligations and liabilities under the Contract. Once the maximum limit is reached, Owner may consider the termination of contract and/or shall have the discretion of getting executed the work from the Contractor with the maximum limit of Liquidated damages. Any such recovery on account of the Liquidated damages can be done from the running bills of the Contractor by Owner. 20.3 The Owner shall at its sole discretion upon reaching the maximum LD limit , as an alternative to the Liquidated Damages at its option, get work executed from elsewhere at the risk and cost of the Contractor irrespective of the fact whether the scope of Contract is identical to the original scope of Contract and in case the Owner chooses the alternative course as mentioned, it will be entitled to recover compensation/ damages from the Contractor irrespective of maximum limit prescribed under Clause 20.1. 20.4 The Owner may by giving (01) one-month notice to the Contractor cancel the Contract without prejudice to the Owner’s right under Clauses 20.1,20.2 and 20.3 or any other provisions contained in the Contract to determine the Contract and claim damages from the Contractor. 20.5 No bonus will be given for earlier Commissioning of the Facilities or part thereof.
5 | Addition of clause no. 18 in existing SCC |  | 18 Functional Guarantees (GCC clause 43.1.1) | - | 1. During the Operational Acceptance after providing 03 chances for the PR demonstration, any shortfall in the Performance Ratio (PR) as determined through the PR Test Procedure specified in Section VII, Scope of Work and Technical Specifications, & “PERFORMANCE GUARANTEE TEST PROCEDURE”, will attract imposition of penalty. For every 0.01 shortfall in PR below the committed PR value, a penalty of 1% of the total Contract Value (i.e., total sum of all the Supply, Service nd absolute value of O & M Contract) shall be levied. In case the Contract Performance Security has already been encashed on count of any default/delays, the penalty amount will be recovered from any due payments to the contractor. In case the lant PR Shortfall is more than 0.05 than the specified PR value, then the total plant will be accepted on as-is basis & the total Contract Performance Security submitted by the contractor will be forfeited & payments linked to operational acceptance will not be made. 2. During the demonstration of yearly CUF, any shortfall from specified CUF shall attract the LD @ INR 5.65/kWh for each unit shortfall. The CUF shall be calculated as per the formula mentioned Section VII, Scope of Work and technical Specifications. Shortfall in CUF during any year may be compensated against excess achieved CUF during previous or subsequent years subject to total CUF over the O&M Period being in accordance with the committed CUF. LD levied, if any, on account of shortfall in CUF in any year shall be refunded when the same is compensated through excess CUF in subsequent years. Determination of LD on account of shortfall, if any, shall be made after such adjustment, upto excess CUF which is not already accounted in an earlier year. If the Contractor fails to achieve 10-year cumulative CUF at the end of O&M period, then the Contractor will pay compensation to Owner an amount equal to the Net Present Value (NPV) of the estimated revenue loss due to shortfall in CUF for 11th to 25th year calculated at a discount factor of 9.08% as below. Where, COM is the compensation payable to Owner in INR Eg is 10-year cumulative guaranteed generation with reference to the committed CUF in kWh Ea is 10-year cumulative actual generation in kWh C is tariff of INR 5.00/kWh. 3.In case the Project fails to generate any power continuously for 1 month any time during the O&M period, apart from the force majeure and grid outages as certified by competent authority, it shall be considered as “an event of Contractor’s default”. In the case of default, the entire Contract Performance Security will be forfeited & the Owner may terminate the O&M contract. 4.Liquidated damages during O&M period against breakdown of other Infrastructure of Plant which doesn’t affect the generation of power, directly such as but not limited to civil infrastructure, water supply system/network, other Infrastructure developed by the Contractor as a Scope of Work for the Project (Section-VII: Scope of Works & Technical Specifications) shall be penalized @ Rs.1000/day, per incident of breakdown reported beyond 07 Days of such reporting. Cumulative value of such penalty shall be limited to 50% of yearly O&M cost. 5.The Liquidated Damages as specified on account of delays and on account of deviations in Functional Guarantees as above shall be assessed and levied independent of each other.
6 | SCC | 8 of 13 | 10 Contract Performance Security (GCC clause 24) | First Stage (Supply and Services): The value of the Contract Performance Security shall be 5% (Five percent) of the Contract Value (i.e., total sum of the Supply & Service Contract) | First Stage (Supply and Services): The value of the Contract Performance Security shall be 10% (Ten percent) of the Contract Value (i.e., total sum of the Supply & Service Contract)
7 | General | - | Payment Order Instrument (POI) | - | "Payment on Order Instrument (POI) against EMD and PBG issued by Indian Renewable Energy Development Agency (IREDA) shall not be acceptable under the subject tender. The relevant provision of the tender document and PPA hereby stand modified to the above effect.