## Amendment1
SOLAR ENERGY CORPORATION OF INDIA LIMITED
New Delhi
No. SECI/C&P/OP/11/0002/26-27/Amendment-01 |  |  |  | Date: 28/07/2026 | Dated:
Amendment-01 to the RfS (RfS No. SECI/C&P/OP/11/0002/26-27 Dated 24.06.2026)
S. No. | Document | Clause No. | Existing Clause | Proposed Modifications/Amended
1 | Scope of Works | 1
2 | Scope of Works | 5.22 | Procurement of conductors for Reconductoring of 4 -5 km stretch of existing 220 kV overhead transmission lines from 300 MW Pooling substation, Ramagiri to Pavagada ISTS Substation. | Procurement of conductors for Reconductoring of 4 -5 km stretch of existing 220 kV overhead transmission lines from 300 MW Pooling substation, Ramagiri to Pavagada ISTS Substation. Existing Conductor: AL59 MOOSE Replacement Conductor: ACSS 378
3 | Scope of Works | 6.17 | Installation, testing and commissioning of the 33/220 kV Transformer Bay, including extension of the existing 220 kV bus, complete testing of all equipment, and integration of Bay Protection Units (BPUs) and Bay Control Units (BCUs) with the existing Substation Automation System (SAS) at SECI’s 300 MW Pooling Substation at Ramagiri. Note: Refer SA-B: Indicative SLD | Installation, testing and commissioning of the 33/220 kV Transformer Bay, including extension of the existing 220 kV bus, complete testing of all equipment, and integration of Bay Protection Units (BPUs) and Bay Control Units (BCUs) with the existing Substation Automation System (SAS) at SECI’s 300 MW Pooling Substation at Ramagiri. Bus Short Circuit Level shall be considered as 50 kA for 1 sec. Note: Refer SA-B: Indicative SLD
4 | Scope of Works | 6.19 | Reconductoring of 4 -5 km stretch of existing 220 kV overhead transmission lines from 300 MW Pooling substation, Ramagiri to Pavagada ISTS Substation. | Reconductoring of 4 -5 km stretch of existing 220 kV overhead transmission lines from 300 MW Pooling substation, Ramagiri to Pavagada ISTS Substation. Existing Conductor: AL59 MOOSE Replacement Conductor: ACSS 378
5 | Scope of Works | 7.4 | Clearing plant site and transmission line corridor by cutting of trees, bushes and shrubs including disposal of waste material. | Clearing plant site and transmission line corridor by cutting of trees, bushes and shrubs including disposal of waste material. Additionally, Contractor shall re-route the 11 kV Transmission Lines which presently fall within the offered land parcels.
6 | Technical Specifications | 14.1 | Table 1: Supply-Specific Ratings and Requirements | Table 1: Supply-Specific Ratings and Requirements
7 | O&M Agreement ANNEXURE-2 Generation Guarantee for Solar Plant | 1. C | Generation Guarantee During O&M: The bidder shall guarantee the Target Generation (GTN) as per PVSyst document finalized during detailed engineering and modified as per O&M Target Generation Test (OTGT) at plant end ABT meter, (i.e., at 220kV near to 33/220 kV pooling substation) after successful O&M Target Generation Test. The annual target generation during O&M shall be calculated as follows- G_T1=G_(TS_ref)×RCF×OTF×[1-DF]; For Year 1 G_TN=G_T1×RCF×OTF×[1-(N-1)×DF]; For Year 2 and onwards Where- GTN - Target generation during Nth O&M year (in kWh) GT_ref - Generation finalized (evaluated) during detailed Engineering (in kWh) N – Year of operation RCF - Radiation Correction Factor; RCF=〖GHI〗_meas/〖GHI〗_ref (Note: Kindly refer to GA-H: Functional Guarantee (FG) Test Procedure) GHImeas - Measured Global Horizontal Insolation during the O&M period (in kWh/m2) GHIref - Reference Global Horizontal Insolation (as per relevant cause of SA-B: Project-Specific Technical Details of Tender Document) OTF - O&M Target Generation Factor: Ratio of achieved generation during OTGT Period to Radiation Corrected Target generation for OTGT period DF – Module degradation factor (in %) (Note: DF shall be provided to Successful bidder based on the module supplied by the Employer. GN - Measured Generation during Nth the O&M period (in kWh) (Actual Generation) | Generation Guarantee During O&M: The bidder shall guarantee the Target Generation (GTN) as per PVSyst document finalized during detailed engineering and modified as per O&M Target Generation Test (OTGT) at the installed TVM meter at the 33 kV Termination Point after successful O&M Target Generation Test. The annual target generation during O&M shall be calculated as follows- G_T1=G_(TS_ref)×RCF×OTF×[1-DF]; For Year 1 G_TN=G_T1×RCF×OTF×[1-(N-1)×DF]; For Year 2 and onwards Where- G_T1, GTN - Target generation duringFirst and Nth O&M year (in kWh), after including deemed generation (lost due to curtailment) during O&M Year, following procedure detailed in Clause 5.6 of GA-H: FG Test Procedure Note: Contractor shal maintain a proper record of Energy Curtailed due to Load Flow Limitations (Grid and/or Battery) GT_ref - Generation finalized (evaluated) during detailed Engineering (in kWh) N – Year of operation RCF - Radiation Correction Factor; RCF=〖GHI〗_meas/〖GHI〗_ref (Note: Kindly refer to GA-H: Functional Guarantee (FG) Test Procedure) GHImeas - Measured Global Horizontal Insolation during the O&M period (in kWh/m2) GHIref - Reference Global Horizontal Insolation (as per relevant cause of SA-B: Project-Specific Technical Details of Tender Document) OTF - O&M Target Generation Factor: Ratio of achieved generation during OTGT Period to Radiation Corrected Target generation for OTGT period DF – Module degradation factor (in %) (Note: DF shall be provided to Successful bidder based on the module supplied by the Employer. GN - Measured Generation during Nth the O&M period (in kWh) (Actual Generation)
8 | GA H - FG Test Procedure | 5.5.1 | Metering point for Solar PV Plant shall be as per the Scope of Works of this Tender Document | Metering point for Solar PV Plant shall be at the 33 kV Termination Point as per the Scope of Works of this Tender Document for the purpose of Generation Guarantees
9 | GA H - FG Test Procedure | 5.5.2 | The Actual Generation (Ga) at the Solar Plant End TVM/ABT meter shall be noted at regular intervals which shall be calculated for OTGT period as follows – | The Actual Generation (Ga) at the installed TVM Meter at 33 kV Termination Point shall be noted regular intervals which shall be calculated for OTGT period as follows –
10 | GA D - SCADA Schematics |  |  | Revised Annexure
11 | SA D - Operational Philosophy for Forecasting, Scheduling and Dispatch of the 50 MW FDRE Plant |  |  | New Annexure
12 | SECTION - VII SUB-SECTION C | Clause 11.3 (Page 21 of 57) | Min. depth of foundation for all buildings and plinth for open installations shall be 1.5 m below NGL. Min. depth of foundation for steps in brick and concrete masonry shall be min. 450mm below FGL. For all other structures, min. depth of foundation shall be 1.0 m unless specified otherwise. | Unless noted otherwise, depth of foundation shall be as per the recommendations of the geotechnical investigation report. Min. depth of foundation for steps in brick and concrete masonry shall be min. 450mm below FGL.
13 | SECTION - VII SUB-SECTION C | Clause 3.8 (Page 8 of 57) | The report shall also include ground water analysis (water sample collected from bore well) to ascertain its suitability for construction purposes, recommendations for type of cement, grade of concrete & minimum cement content as per prevalent soil characteristics with respect to presence of aggressive chemicals and environment exposure conditions as per relevant BIS specifications. However, minimum grade of concrete shall be as specified under Cl.Error! Reference source not found. 'Concrete Works' | The report shall also include ground water analysis (water sample collected from bore well) to ascertain its suitability for construction purposes, recommendations for type of cement, grade of concrete & minimum cement content as per prevalent soil characteristics with respect to presence of aggressive chemicals and environment exposure conditions as per relevant BIS specifications. However, minimum grade of concrete shall be as specified under Cl. 14. ‘Concrete Works’.
14 | SECTION - VII SUB-SECTION C | Clause 3.10 (Page 10 of 57) | All buildings and Plinth for Open installations (MCR, ICR etc.), Transformer yard, Switchyard and Sub-station area shall have levelled ground as detailed under Clause No. Error! Reference source not found. | All buildings and Plinth for Open installations (MCR, ICR etc.), Transformer yard, Switchyard and Sub-station area shall have levelled ground as detailed under Clause No. 5 'Area Grading and Land Development'.
15 | SECTION - VII SUB-SECTION C | Clause 13.7 (Page 26 of 57) | Material specifications & coating for structural steel works: | Material specifications & coating for structural steel works:
16 | SECTION - VII SUB-SECTION C | Clause 13.8 (Page 26 of 57) | The primary loads and load combinations for design of MMS structure shall be as specified under Clause No. Error! Reference source not found.. The design shall be done by Working stress method and no increase in allowable stress shall be permitted. | The primary loads and load combinations for design of MMS structure shall be as specified under Clause No. 10 'Design Loads'. The design shall be done by Working stress method and no increase in allowable stress shall be permitted.
17 | SECTION - VII SUB-SECTION C | Clause 7.10 (Page 16 of 57) | In case of rectangular drain, the thickness of the wall shall be checked against structural stability under action of the design loads as specified in Cl. No. Error! Reference source not found. ‘Design Loads’. However, the min. wall thickness shall be 230mm, 300mm and 125mm respectively for brick masonry, RR masonry and RCC work, except for garland drain around buildings where the min. wall thickness can be 115mm, 200mm and 100mm respectively for brick masonry, RR masonry and RCC work. | In case of rectangular drain, the thickness of the wall shall be checked against structural stability under action of the design loads as specified in Cl. No. 10 ‘Design Loads’. However, the min. wall thickness shall be 230mm, 300mm and 125mm respectively for brick masonry, RR masonry and RCC work, except for garland drain around buildings where the min. wall thickness can be 115mm, 200mm and 100mm respectively for brick masonry, RR masonry and RCC work.
18 | SECTION - VII SUB-SECTION C | Clause 12.5 (Page 25 of 57) | Unless specified else were, the field trials for initial load tests on concrete and helical/ screw pile shall conform to IS: 2911 (Part 4) & Practice Note-28 (IPENZ Engineers New Zealand) as applicable. The no. and location of such tests shall be as per the provisions stipulated under Cl. No. Error! Reference source not found. | Unless specified else were, the field trials for initial load tests on concrete and helical/ screw pile shall conform to IS: 2911 (Part 4) & Practice Note-28 (IPENZ Engineers New Zealand) as applicable. The no. and location of such tests shall be as per the provisions stipulated under Cl. No. 3.9.3.
19 | SECTION - VII SUB-SECTION C | Clause 16.2.1 (Page 31 of 57) | MCR Buildings For operation & maintenance of SPV Plant, unless otherwise specified elsewhere, Control room cum office area of MCR building shall provide following facilities: • Air-conditioned area (with provision of split A/C unit of adequate capacity) for SCADA room (min. carpet area 32m2), Conference room (min. carpet area 32 m2) & Supervisor cabin (15 m2) and office area (min. carpet area 25 m2) • Switchgear, equipment room(s) as per OEM requirements (can be in a separate building adjacent to the MCR) • Tool room (12.5 m2) • Store cum record room (min. carpet area 15 m2) • Battery room as per requirement (can be in a separate building adjacent to the MCR) • Toilet block with separate gents and ladies wash room facilities (min. total carpet area 12 m2) • Pantry with service platform and utensil washing facilities (min. carpet area 5 m2) • Suitable provision for passage (for smooth movement of O & M personnel), cable trenches, operating area etc. (min. clear width 1500mm) • GI Ladder with hand rail for roof access • MCR Building shall be RCC Framed Structure | MCR Buildings For operation & maintenance of SPV Plant, unless otherwise specified elsewhere, Control room cum office area of MCR building shall provide following facilities: • Air-conditioned area (with provision of split A/C unit of adequate capacity) for SCADA room (min. carpet area 32m2), Conference room (min. carpet area 32 m2) & Supervisor cabin (15 m2) and office area (min. carpet area 25 m2) • Switchgear, equipment room(s) as per OEM requirements (can be in a separate building adjacent to the MCR) • Tool room (12.5 m2) • Store cum record room (min. carpet area 15 m2) • Battery room as per requirement (can be in a separate building adjacent to the MCR) • Toilet block with separate gents and ladies wash room facilities (min. total carpet area 12 m2) • Pantry with service platform and utensil washing facilities (min. carpet area 5 m2) • Suitable provision for passage (for smooth movement of O & M personnel), cable trenches, operating area etc. (min. clear width 2000mm) • RCC Staircase with SS hand rail for roof access • MCR Building shall be RCC Framed Structure • Handrails and ladder pipes shall be 32 mm nominal bore SS pipes (medium class) with SS 304 Grade
20 | SECTION - VII SUB-SECTION C | Clause 16.1.4 | The contractor shall submit the proposed equipment layout drawings to the Engineer for approval before development of Architectural drawings. The building layout, exterior elevations shall be aesthetically designed following good architectural practices to get a pleasant look. Horizontal/ vertical bands through projections/ groves in external plaster may be provided to break the monotony. Roof slab shall have projection of 450mm beyond the external walls with 230 THK brick parapet wall of 450 mm clear height all-around which shall form a projected band at roof level. For weather protection all doors and windows shall be provided with 450mm wide RCC chajja. However, chajja for rolling shutter shall be 750mm wide. | The contractor shall submit the proposed equipment layout drawings to the Engineer for approval before development of Architectural drawings. The building layout, exterior elevations shall be aesthetically designed following good architectural practices to get a pleasant look. Horizontal/ vertical bands through projections/ groves in external plaster may be provided to break the monotony. Roof slab shall have projection of 450mm beyond the external walls with 230 THK brick parapet wall of 600 mm clear height all-around with additional 600mm height SS Hand rail (Total height 1200mm) which shall form a projected band at roof level. For weather protection all doors and windows shall be provided with 450mm wide RCC chajja. However, chajja for rolling shutter shall be 750mm wide.
21 | SECTION - VII SUB-SECTION C | Clause 18.1 (Page 36 of 57) | Doors, windows, louvers and ventilators shall be made of AL sections (minimum average thickness 2.5mm), industrial grade, anodized (grade AC25, min. thickness 25 micron conforming to IS: 1868) or with polyester powder coating (Total DFT 50 microns conforming to IS: 13871) and shall be of approved make & colour shade. All sections, fittings and fixtures shall be anodized (min. thickness of coating 20 micron). The window and door shutters shall be of clear float/ wired/ ground glass as per design/ functional requirements. The doors in toile area shall be of steel frame with solid core (MDF) flush shutter, 35mm thick, with laminated finish on both sides conforming to IS: 2202. | Doors, windows, louvers and ventilators shall be made of AL sections (minimum average thickness 2.5mm), industrial grade, anodized (grade AC25, min. thickness 25 micron conforming to IS: 1868) or with polyester powder coating (Total DFT 50 microns conforming to IS: 13871) and shall be of approved make & colour shade. All sections, fittings and fixtures shall be anodized (min. thickness of coating 20 micron). The window and door shutters shall be of clear float/ wired/ ground glass as per design/ functional requirements. The doors in toilet area shall be uPVC flush door with a uPVC frame reinforced core, a wall thickness of 2.5 mm to 3 mm, and panel thicknesses between 24 mm and 30 mm.
22 | SECTION - V SPECIAL CONDITIONS OF CONTRACT (SCC) | 16 A in Schedule of Rates & Payments (GCC clause 80.1) | … A. The payment for the Supply Portion of the First Contract (Supply Contract) shall be made as per the following terms and conditions: i) Interest free initial advance (OPTIONAL) of 10% (ten) of the Contract Value (i.e., total sum of all the Supply Contract) shall be released to the contractor upon receipt of unconditional acceptance of CA, detailed Performa invoice of contractor and against submission of unconditional & irrevocable Advance Bank Guarantee (ABG, Format 33) with a validity period up to date of final commissioning total amounting to 110% of total advance amount. The ABG needs to be submitted in addition to the Contract Performance Security. ii) Sixty (60%) payments shall be paid against dispatch of Material from Manufacturer’s work on submission of documents (except Advance Bank Guarantee) indicated under clause i) above, Contractor’s detailed invoice & packing list identifying contents of each shipment, evidence of dispatch, Manufacturer’s/ Contractor’s Guarantee certificate of Quality and MDCC (Material Dispatch Clearance Certificate) issued by Employer's authorized representative in original. iii) Twenty Five (25%) payments shall be paid on Pro rata basis against supply, receipt and acceptance of Materials at site on submission of documents (except Advance Bank Guarantee) indicated under clause i) above, Contractor’s detailed invoice & packing list identifying contents of each shipment, evidence of dispatch (GR/ LR copy), Manufacturer’s/ Contractor’s Guarantee certificate of Quality, submission of the certificate by the Executing Agency’s authorized representative that the item(s) have been received and MDCC (Material Dispatch Clearance Certificate) issued by Employer's authorized representative in original. * In case the Interest free initial advance (OPTIONAL) of 10% of the Contract Value is not availed by the contractor, then this 10% payment amount will be payable along with the point No A iii) payment milestone against supply, receipt and acceptance of Materials at site. * In case the interest free advance is availed by the Contractor and no progress/work is executed at site till the commissioning period or if the contract is terminated due to default of contractor as mentioned under the Contract/tender, thereby not adjusting the advance amount timely, the entire advance amount will be recovered from the Contractor along with one-year SBI MCLR rate. The advance bank guarantee may be reduced in proportion to the value of the 10% advance payment adjusted against plant and equipment delivered to the site, as evidenced by shipping and delivery documents. (iv) Final Five percent (5%) payment of Supplies shall be paid against submission of the BG of the equivalent amount & against the Operational Acceptance of the plant Facility pursuant to successful O&M Target Generation Test including submission of all as-built drawings and O&M manual. This BG shall be valid for a period of 18 (Eighteen) months from the date of its issuance & will be released after target generation demonstration on completion of first year of O&M, pursuant to the submission of all requisite documentation up to the final acceptance of the Plant facilities. However, in case of any delay, the BG shall be extended suitably. ......... | ....... A. The payment for the Supply Portion of the First Contract (Supply Contract) shall be made as per the following terms and conditions: i) Interest free initial advance (OPTIONAL) of 10% (ten) of the Contract Value (i.e., total sum of all the Supply Contract) shall be released to the contractor upon receipt of unconditional acceptance of CA, detailed Performa invoice of contractor and against submission of unconditional & irrevocable Advance Bank Guarantee (ABG, Format 33) with a validity period up to date of final commissioning total amounting to 110% of total advance amount. The ABG needs to be submitted in addition to the Contract Performance Security. ii) Fifty (50%) payments shall be paid against dispatch of Material from Manufacturer’s work on submission of documents (except Advance Bank Guarantee) indicated under clause i) above, Contractor’s detailed invoice & packing list identifying contents of each shipment, evidence of dispatch, Manufacturer’s/ Contractor’s Guarantee certificate of Quality and MDCC (Material Dispatch Clearance Certificate) issued by Employer's authorized representative in original. iii) Twenty (20%) payments shall be paid on Pro rata basis against supply, receipt and acceptance of Materials at site on submission of documents (except Advance Bank Guarantee) indicated under clause i) above, Contractor’s detailed invoice & packing list identifying contents of each shipment, evidence of dispatch (GR/ LR copy), Manufacturer’s/ Contractor’s Guarantee certificate of Quality, submission of the certificate by the Executing Agency’s authorized representative that the item(s) have been received and MDCC (Material Dispatch Clearance Certificate) issued by Employer's authorized representative in original. * In case the Interest free initial advance (OPTIONAL) of 10% of the Contract Value is not availed by the contractor, then this 10% payment amount will be payable along with the point No A iii) payment milestone against supply, receipt and acceptance of Materials at site. * In case the interest free advance is availed by the Contractor and no progress/work is executed at site till the commissioning period or if the contract is terminated due to default of contractor as mentioned under the Contract/tender, thereby not adjusting the advance amount timely, the entire advance amount will be recovered from the Contractor along with one-year SBI MCLR rate. The advance bank guarantee may be reduced in proportion to the value of the 10% advance payment adjusted against plant and equipment delivered to the site, as evidenced by shipping and delivery documents. (iv) Seven and Half percent (7.5 %) payments shall be paid against successful erection, testing and pre-commissioning of equipment(s)/Project duly certified by Engineer-in Charge/Head of Project on pro rata basis. (v) Two and Half percent (2.5 %) payments shall be paid against successful commissioning of project on pro rata basis. (vi) Ten percent (10 %) payment of Supplies shall be paid against submission of the BG of the equivalent amount & against the Operational Acceptance of the plant Facility pursuant to successful O&M Target Generation Test including submission of all as-built drawings and O&M manual. This BG shall be valid for a period of 18 (Eighteen) months from the date of its issuance & will be released after target generation demonstration on completion of first year of O&M, pursuant to the submission of all requisite documentation up to the final acceptance of the Plant facilities. However, in case of any delay, the BG shall be extended suitably. ........
23 | SECTION - V SPECIAL CONDITIONS OF CONTRACT (SCC) | 16 B (iii) (a) in Schedule of Rates & Payments (GCC clause 80.1) | … iii) For Civil & Allied works portion, of the First contract, the payment shall be made as detailed below: (a) Eighty Percent (85%) of the total price of Civil Works shall be paid progressively on certification by the Project Manager/ Engineer In - Charge for the quantum of work completed/ Milestones achieved after successful clearance of quality check points involved in the quantum of work. ......... | … iii) For Civil & Allied works portion, of the First contract, the payment shall be made as detailed below: (a) Eighty-Five Percent (85%) of the total price of Civil Works shall be paid progressively on certification by the Project Manager/ Engineer In - Charge for the quantum of work completed/ Milestones achieved after successful clearance of quality check points involved in the quantum of work. .........