## Prebid Queries
SOLAR ENERGY CORPORATION OF INDIA LIMITED
New Delhi
No. SECI/C&P/OP/11/0002/26-27/Clarification-01 | [5 empty] | Dated: 28/07/2026
(RfS title) : Clarifications to the queries on the RfS (RfS No. SECI/C&P/OP/11/0002/26-27 dated 24.06.2026)
S. No. | Documents | Clause No. | Existing Clause | Proposed Modifications | Rationale/Remarks | SECI's response
1 | TS-Electrical | 14.1 | BESS Availability-98% | BESS Availability-95% | The BESSD shall guarantee a minimum system availability of 95% on Annual basis for charging cycles. KREDL: KREDL/07/SG/F-2052/250 MW/500MWh/2025-26 dtd 16.06.2026 | Terms and Conditions of the Tender shall prevail
2 | BDS | 2 | IIA.The bidder should have experience in execution of Ground mounted Solar PV Projects as a Developer of Grid-connected Solar PV Power Plant(s) of cumulative Capacity not less than 35 MW (Thirty-Five) MW in last seven years as on last date of bid submission. However, such Grid connected Solar PV Power Plant capacity must have been in satisfactory operation for at least six (06) months prior to the last date of bid submission. AND IIB. The bidder should have experience in execution of Ground mounted Solar Projects as a Developer of at least 02 (Two) Grid connected Solar PV Power Plant Projects having an individual capacity of 7 (Seven) MW or above in last seven years and till last date of bid submission. However, such Grid connected Solar PV Power Plant capacity must have been in satisfactory operation for at least six (06) months prior to the last date of bid submission | IIA.The bidder should have experience in execution of Ground mounted Solar PV Projects as a Developer of Grid-connected Solar PV Power Plant(s) of cumulative Capacity not less than 35 MW (Thirty-Five) MW in last seven years as on last date of bid submission. However, such Grid connected Solar PV Power Plant capacity must have been in satisfactory operation for at least six (06) months prior to the last date of bid submission. AND IIB. The bidder should have experience in execution of Ground mounted Solar Projects as a Developer of at least 01 (One) Grid connected Solar PV Power Plant Projects having an individual capacity of 7 (Seven) MW or above in last seven years and till last date of bid submission. However, such Grid connected Solar PV Power Plant capacity must have been in satisfactory operation for at least six (06) months prior to the last date of bid submission | The Bidder should have designed, supplied, erected/ supervised erection and commissioned/ supervised commissioning of Solar Photo Voltaic (SPV)/Wind based grid connected power plant(s) of cumulative installed capacity of 40 MWAC or higher, out of which at least one plant should have been of 10 MWAC or higher capacity. The reference plant of 10 MWAC or higher capacity must have been in successful operation for at least six (6) months prior to the date of techno commercial bid opening. NTPC: NREL-CS-5823-004(BESS1)-9 dtd 16/06/2026 | Terms and Conditions of the Tender shall prevail
3 |  |  | Not mentioned in Tender Documents | Kindly provide the Capacity Utilization Factor for Solar plant |  | CUF is not specified in the subject tender. The bidder shall guarantee the Target Generation (GTN) for each O&M year. Bidder is free to propose his design of the solar plant including solar plant layout, solar block sizing, inverter sizing, inverter-transformer sizing etc. subject to meeting the boundary conditions/design parameters as specified in Specific Annexure B. The GTN value is finalized during detailed engineering based on the approved PVSyst report and benchmarked during the first O&M Target Generation Test (OTGT). Procedure is detailed in GA-F_FG Test Procedure.
4 | Specific Annexure-B | 3 | PV Module Wattage - 605Wp | Kindly provide the technical datasheet for this PV Module |  | PV Modules are supplied by the Owner as Free-Issue Items. Bidders shall assume the specified ratings for bid engineering. The final make and PAN files will be shared during detailed engineering with the successful bidder.
5 | SOW | 1 | Available Land Area-Refer to SA-A: Tentative Land Layout | During our site visit, the available land is only 210 acres only. But we require atleast 280 acres for Solar, BESS and associated pooling sub-station. Kindly clarify. |  | Land Acquisition is under process. Enumbrance free land of required area shall be made available for plant deployment. KMZ shall be shared once Land Acquisition is complete.
6 |  |  | Not mentioned in Tender Documents | During our site visit, Routing of electric poles of AP electricity board is under bidder scope. Kindly clarify and if it is in bidder scope please provide the re-route map. |  | Please refer to Amendment No. 5. Re-route map shall be shared subsequently with the succesful bidder.
7 | BDS | 4.1 | JOINT VENTURE & CONSORTIUM CONDITIONS | The Lead partner of the JV/Consortium shall meet individually 100% of Technical Eligibility Conditions given at para above. | Kindly amend The Lead Partner of the JV/Consortium shall Collectively meet 100% of the Technical Eligibility criteria along with other Consortium members | Terms and Conditions of the Tender shall prevail
8 | SS-A, Cl.1 Project Particulars, Pg.3 | Cl.1 Project Particulars, | Cumulative Inverter (PCU) AC Capacity and Cumulative Inverter (PCS) Capacity are shown as "XX MVA" to deliver 70 MW / 25 MW at 50°C at POI. | The MVA rating field for both Solar PCU and BESS PCS capacity is left blank ("XX"). Kindly confirm whether the Bidder is to independently size and declare this MVA rating based on design temperature de-rating and reactive power requirement, or whether SECI will issue a minimum benchmark MVA figure before bid submission. |  | Bidders must independently size and declare the MVA ratings for both Solar PCU and BESS PCS to deliver the specified active power at the POI at the design ambient temperature of 50°C. The means of achieving Reactive requirement shall be finalized during detailed engineering based on the grid interconnection studies and may include an appropriate combination of PCUs, PCSs, and/or SVGs.
9 | SS-A, Cl.1, Dispatchable BESS Energy Table, Pg.4 | Cl.1, Dispatchable BESS Energy | Year-wise dispatchable energy table is furnished only up to Year 10 (Year 1: 50 MWh down to Year 10: 38.75 MWh), while the note refers to "Table entries from Year 6 to 12" for sizing purposes. | The table provided lists only Years 1–10, whereas the accompanying note references Years up to 12. Kindly furnish the complete year-wise dispatchable energy table up to Year 12 (or clarify the applicable degradation trajectory beyond Year 10) to enable correct BESS augmentation sizing. |  | Please refer to Amendment No. 1
10 | SS-A, Cl.3 Responsibility Matrix, Pg.7 | Cl.3 Responsibility Matrix | Responsibility matrix allocates design, supply, installation, testing/commissioning line items between Owner/EPC contractor package 1/EPC contractor package 2 | Kindly confirm whether the Responsibility Matrix table is exhaustive or indicative; specifically request clarification on ownership of interconnection works beyond the Plant Metering Point (220 kV side) up to the ISTS pooling point, and whether any grid-side augmentation/strengthening cost falls under |  | Responsibility Matrix is indicative. Scope includes design, supply, and installation up to the Point of Interconnection (POI), defined as the 220 kV Busbar at SECI's 300 MW Pooling Substation. This includes the transformer bay and additional 4 km of conductor mounting on existing 220kV towers from the 300 MW pooling substation till the remote Grid Substation.
11 | Technical Document | Clause 5.17 Page No. 18 | In addition to the feeder panels for the Solar and BESS Feeders, two (2) nos. of feeder panels shall be provided for two feeders routed from the Wind Package along with one (1) no. of additional feeder panel as spare. Connecting wind feeders to the panels shall be responsibility of the Contractor | Kindly clarify whether the Contractor's scope falls under Package-1 or Package-2. Since the power generated by the Package-2 (Wind) Contractor is proposed to be injected at the Pooling Substation (PSS) being developed under Package-1, please confirm whether the incoming bay required for wind power injection is under the scope of Package-1 Contractor or Package-2 Contractor. |  | Bidder scope is restricted to Works mentioned under Package 1 (subject tender). The Package-1 Contractor (Solar + BESS) is responsible for providing the pooling switchgear, which must include 3 Nos. feeders dedicated for the Wind package. Laying of 33 kV Cables from the double pole structures where the wind reticulation system is terminated is within the scope of the Wind Package Contractor.
12 | IFB Contractual Documents | Clause 1.4 Page No. 6 | The 50 MW Renewable Energy Hybrid Project (on FDRE basis) has been divided into two packages, which shall be awarded through separate tenders | Further, in the event of any shortfall in achieving the 50 MW FDRE obligation due to delay, underperformance, or non-availability attributable to the Package-2 (Wind) Contractor, kindly clarify the methodology for determining responsibility and the criteria for levying penalties. Specifically, please confirm whether such penalties shall be imposed solely on the Package-2 Contractor or apportioned between the contractors based on the attributable shortfall. |  | Shortfall in achieving 50 MW FDRE shall not be attributable to Package 1 Contractor. Scheduling of the Power shall be within SECI's scope. Package 1 Contractor shall be responsible for demonstrating Performance Guarantees at time of commissioning and O&M Period as per Tender (OTGT Test). Please refer to Amendment No. 7.
13 | SS-A, Cl.1, Power Evacuation, Pg.4–5 | Cl.1, Power Evacuation | SA-B: Indicative Single Line Diagram (SLD); Note elsewhere states "The SA-B Indicative SLD is for reference only and not a final design." | Please confirm whether the final SLD, switchyard bay configuration and metering scheme will be issued as part of the LOA/detailed engineering, and whether any change in scheme (e.g., single vs. double bus, TVM location) between tender stage and final design will be treated as a Change in Scope / Change in Law event for cost and time purposes. |  | The indicative SLD is for reference only and not a final design. The contractor is responsible for the final engineering of all equipment, protection, and metering systems to ensure grid compliance, which shall be subject to review and approval by SECI.
14 | SS-A, Cl.1, Supply of PV Modules, Pg.3 | Cl.1, Supply of PV Modules | "Supply of PV Modules at the Project Site shall be in the Scope of the Owner... delivered as Free-Issue Items." | Kindly clarify: (i) the point of delivery (ex-factory / at site) and mode of transport for Owner-supplied modules; (ii) the responsibility and cost for unloading, site storage, security and insurance of Free-Issue modules until installation; (iii) the liability apportionment for transit/storage damage or shortage between Owner and Contractor; and (iv) the module delivery schedule vis-à-vis the Contractor's execution schedule, including any provision for schedule relief if module delivery is delayed by the Owner. |  | The provisions of Clause 5 under Section VII, Sub-Section A ("Scope of Works") are self-explanatory and require no further clarification
15 | Technical Document | Page No 362 | The laititude & longitude are not correct as per the tender drawing. | Kindly share the KMZ file of the exact land allocated for this project. |  | Land Acquisition is under process. Enumbrance free land of required area shall be made available for plant deployment. KMZ shall be shared once Land Acquisition is complete.
16 | SS-B, TS-Electrical – BESS Functional Guarantee, Pg.5–6 / GA-H | Pg.5–6 / GA-H | RTE (Round Trip Efficiency) guarantee ≥ 85% at 33kV BESS Termination Point, including auxiliary consumption, measured during PG Test. | Kindly specify (i) the reference ambient temperature and SOC window at which the 85% RTE guarantee is to be demonstrated, (ii) whether RTE degradation over the O&M period/design life is permitted and, if so, the allowable annual degradation trajectory, and (iii) the BESS cell chemistry, C-rate and minimum cycle life (at specified DoD) that the Employer expects, if any, as these are not explicitly specified in the tender. |  | (i) The guaranteed Round Trip Efficiency (RTE) of 85% shall be demonstrated during the Performance Guarantee (PG) Test under the prevailing site ambient conditions at the time of testing. The State of Charge (SoC) operating window shall be as per the Contractor's approved BESS design. Bidders shall appropriately account for the maximum site ambient temperature and other operating conditions while designing the BESS to ensure compliance with the guaranteed RTE. (ii) The Tender does not require monitoring or verification of RTE during the O&M period. During O&M, performance shall be assessed based on the minimum dispatchable energy requirements specified in the Project Particulars / Scope of Works, and not on measured Round Trip Efficiency. (iii) The Technical Specifications are chemistry-agnostic and do not mandate any specific battery cell chemistry. The applicable requirements regarding C-rate and minimum cycle life are specified in Table 2 of Clause 14.1 of the Technical Specifications and shall be complied with by the successful bidder.
17 | SS-B, Reactive Power Capability, Pg.3 | Pg.3 | Reactive power capability within PF range 0.95 lagging to 0.95 leading at 220kV POI, achievable "by combination of PCUs, PCSs or SVGs." | Please clarify whether provision of dedicated SVG/STATCOM (if required to meet reactive power compliance) is to be included in the base bid scope by default, or only if PCU/PCS combination is demonstrably insufficient — and who bears the cost/schedule impact if SVG is required after detailed engineering. |  | Compliance with all applicable Grid Code requirements, including reactive power and voltage control requirements, shall be the responsibility of the Successful Bidder. The Bidder shall carry out the required grid interconnection studies and design the plant accordingly. If additional equipment, including but not limited to PCUs, PCSs, SVGs, or STATCOMs, is required to achieve compliance, the same shall be deemed to be within the Contractor's scope of supply and shall be provided without any additional cost or extension of time to the Employer.
18 | GA-B: Mandatory Spares, Pg.1 of 9 | Pg.1 of 9 | Mandatory spares list specified for PV-side equipment (connectors, SCB, PCU/inverter components, inverter transformer, power transformer) as % of supply or fixed sets. | Kindly confirm whether a corresponding Mandatory Spares list for BESS-side equipment (PCS, battery racks/modules, BMS, HVAC, fire suppression system, container electricals) will be separately issued, as this does not appear in the furnished Mandatory Spares annexure. |  | Please refer to S. No. 19 of the GA-B: Mandatory Spare
19 | Technical Document | Clause No. 5.22 Page No. 19 | Procurement of conductors for Reconductoring of 4 -5 km stretch of existing 220 kV overhead transmission lines from 300 MW Pooling substation, Ramagiri to Pavagada ISTS Substation | Kindly clarify the type and technical specifications of the existing conductor proposed for replacement. Further, please confirm the type, size, rating, and complete technical specifications of the replacement conductor to be provided under the scope of work. |  | Existing Conductor: AL59 MOOSE Replacement Conductor: ACSS 378 Please refer to Amendment No. 2 and 4
20 | SECTION - VII | 7 Civil Works | 2.6 | Positions, both in plan and elevation, of all natural and artificial features in the area like waterways, railway tracks, trees, cultivation, houses, fences, pucca and kutcha roads including culverts and crossings, foot tracks, other permanent objects like telephone posts and transmission towers etc | Please ensure that the project plot shall be free from any unhindered obstacles like electricity poles, transmission towers waterways, railway tracks & trees etc. | Assesment of any such hinderences and site development to make the site ready for project installation shall be in the scope of the Bidder.
21 | SECTION - VII | 7 Civil Works | 3 Geotechnical Investigations | However, minimum grade of concrete shall be as specified under Cl.Error! Reference source not found concrete works. | Please specify the minimum grade of concrete. | Refer to Sl. No. 13 of Amendment
22 | SECTION - VII | 7 Civil Works | 3.1 | All buildings and Plinth for Open installations (MCR, ICR etc.), Transformer yard, Switchyard and Sub-station area shall have levelled ground as detailed under Clause No. Error! Reference source not found.. | we don't find any clause for levelled ground. Please provide the clause regarding the levelled area. | Refer to Sl. No. 14 of Amendment
23 | SECTION - VII | 7 Civil Works | 5.4 | The contractor is responsible for making the site ready and easily approachable by clearing bushes, felling of trees (mandatory permissions/ licenses/ statutory clearances from competent authorities if required for cutting of trees, blasting or mining operations, disposal of waste material etc. shall be obtained by the contractor), cutting, filling with selected excavated earth or borrowed earth including identifying borrow areas | Bidder understanding is that No Major site Grading and Levelling is in the scope of Bidder except micro levelling.Also,Bidder is requested to provide the location from where earth material is to be borrowed for land development and filling purpose. | Bidder may visit the site to assess their requirements. Terms and conditions of tender shall prevail.
24 | SECTION - VII | 7 Civil Works | 5.6 | Excess earth, if any, shall be disposed of properly at location as directed by the Engineer. | Please provide the lead distance for disposal of waste material. | This shall be finalized during detailed engineering as per approval from SECI. Terms and conditions of tender shall prevail.
25 | SECTION - VII | 7 Civil Works | 6 | Roads | For BESS area please specify the type of road to be adopted during pre-bid engineering. | Road specifications in BESS area shall be as specified under Cl.40.7 ‘BESS Yard Roads’.
26 | SECTION - VII | 7 Civil Works | 13 Module Mounting Structure (MMS) | 13.7 Material specifications & coating for structural steel works | The table is not readable. | Refer to Sl. No. 15 of Amendment
27 | SECTION - VII | 7 Civil Works | 13 Module Mounting Structure (MMS) | 13.8 The primary loads and load combinations for design of MMS structure shall be as specified under Clause No. Error! Reference source not found.. | Kindly provide primary loads and load combinations for design of MMS structure | Refer to Sl. No. 16 of Amendment
28 | SECTION - VII | 7 Civil Works | 16.2.1 | MCR Buildings | Please provide GA & Architectural view & approx. size/area of MCR building for bidding purpose. | Minimum area requirement for the MCR facility has been provided under Cl 16.2.1. GA & Architectural drawing shall be finalized during Detailed engineering.
29 | Sub-Section A: SOW Page 2 of 27 | 1 Project Particulars | The 50 MW FDRE Project consists of two packages: (i) Package-1: 70 MW Solar PV Power Plant coupled with 25 MW/50 MWh BESS (covered under this tender), and (ii) Package-2: 45.6 MW Wind Power Plant (to be awarded through a separate tender) |  | Please clarify the SOW. Bidders must take into account the Battery Energy Storage System (BESS) and solar SOW, or should they also consider wind energy? | Bidder shall consider only Solar plus BESS SoW
30 | Sub-Section A: SOW Page 2 of 27 | 1 Project Particulars | Cumulative Inverter (PCU) AC Capacity (Solar) XX MVA to deliver 70 MW at 50°C at POI Cumulative Inverter (PCS) Capacity (BESS) XX MVA to deliver 25 MW at 50°C at POI |  | Please confirm The AC Capacity need to be deliver at POI at Which PG test will be Carried Out. | The AC capacity at the POI for the Performance Guarantee (PG) Test shall be determined by the Successful Bidder during detailed engineering based on PVsyst modelling and grid interconnection studies. The Contractor shall ensure compliance with the contractual AC power injection and energy dispatch requirements specified in the Tender.
31 | Sub-Section A: SOW Page 13 of 27 | 5 Procurement & Supply | Solar Cables of appropriate size and rating from PV Modules to SMB / IPC / String Inverter along with straight/Y-connectors/branch connectors, ferrules, conduits, cable ties and other materials required for cable laying and termination at both the ends. |  | Please confirm Monitoring Required in SCB or not. | Monitoring Required in SMB
32 | Sub-Section A: SOW Page 14 of 27 | 5 Procurement & Supply | Power Conditioning Units (Central / String Inverter) of appropriate rating. |  | Please clarify whether there are any specific inverter requirements for the BESS and solar integration, or whether bidders are free to propose the inverter configuration best suited to their system design, subject to compliance with the project's technical requirements. | Bidders are free to propose the inverter configuration best suited to their system design, provided it complies with all applicable requirements of the Tender, including the Technical Specifications and Grid Code.
33 | Single Line Diagram |  | Single Line Diagram |  | As per the Single Line Diagram (SLD), our understanding is that the bidder's scope of work terminates at the 33 kV point where the solar PV, wind, and BESS systems are interconnected. Please confirm if our understanding is correct. | Understanding is incorrect. The Bidder's scope of work includes all Solar PV and BESS works up to the 220 kV interconnection point, including reconductoring of the 4 - 5 km transmission line between the 300 MW Solar Power Plant and the Interconnecting Grid Substation, as specified in the Tender. Please refer Responsibility Matrix and the Indicative SLD furnished with the Tender.
34 | Sub-Section A: SOW Page 18 of 27 | 6 Installation, Testing and Commissioning | Installation, testing and commissioning of the 33/220 kV Transformer Bay, including extension of the existing 220 kV bus, complete testing of all equipment, and integration of Bay Protection Units (BPUs) and Bay Control Units (BCUs) with the existing Substation Automation System (SAS) at SECI’s 300 MW Pooling Substation at Ramagiri. |  | Kindly confirm whether all 33 kV switchgear panels including Solar feeders, BESS feeders, Wind feeder bays, spare feeder bay, protection relays, metering, SAS/SCADA integration and associated control panels are entirely under the EPC Contractor scope without any free-issue material from SECI. | The contractor is responsible for the design, supply, and installation of the CMCS 33 kV Pooling Switchgear, including Solar, BESS, and 3 dedicated Wind feeders, and SCADA. Substation equipment, including Bay Protection Units (BPUs) and Bay Control Units (BCUs), shall be integrated with the existing Substation Automation System (SAS) system housed within the 300 MW Solar Power Plant in Ramagiri owned by SECI.
35 | Sub-Section A: SOW Page 18 of 27 | 6 Installation, Testing and Commissioning | Reconductoring of 4 -5 km stretch of existing 220 kV overhead transmission lines from 300 MW Pooling substation, Ramagiri to Pavagada ISTS Substation. |  | Please confirm the Transmission line Length or loss need to consider | Transmission Line Length: 4 - 5 km Existing Conductor: AL59 MOOSE Replacement Conductor: ACSS 378 Please refer to Amendment No. 2 and 4
36 | Sub-Section B: TS-Electrical Page 11 of 107 | 4.2 Technical Requirements | Winding As per system design requirement |  | Bidder consider Aluminium Winding. | Bidder may propose Aluminum or Copper.
37 | Sub-Section B: TS-Electrical Page 4 of 107 | 2.1 Solar and DC Cables | In case of central inverters, average voltage drop in the cables (from PV Modules to PCU) shall be limited to 1.5 % of the rated voltage. In case of string Inverters, average voltage drop (from PV module to string inverter) shall be limited to 0.5% of the rated voltage drop. |  | In the case of a central inverter configuration, may the bidder consider a 2% DC loss from the PV modules to the Central inverter ? Please confirm. | Terms and Conditions of the Tender shall prevail
38 | Sub-Section B: TS-Electrical Page 33 of 107 | Uninterrupted Power Supply | Pooling Substation UPS system shall comprise of two nos. of UPS of 100% capacity, i.e., two inverters, batteries and UPSDB connected by bus coupler. Sizing of UPS shall be done considering the above-mentioned load at power factor of 0.8 lagging inclusive of 10% design margin at 50 ˚C |  | Please Confirm the UPS size rating Required at 33kV switchgear and on ICR Blocks | Shall be finalised during Detailed Engineering
39 | Sub-Section B: TS-Electrical Page 99 of 107 | 21 | Weather Monitoring System As a part of weather monitoring system, the Contractor shall provide the following measuring instruments with all necessary software and hardware required to integrate with SCADA. |  | Bidder have to consider the WMS Sensor qunatity as per RFP | The contractor must provide WMS Sensors in quantities delineated in Clause 5.35 of the Scope of Works
40 | Sub-Section B: TS-Electrical Page 33 of 107 | 9.2.5 | The battery sizing shall account for suitable temperature correction factors, ageing factors of 1.25, design margin of 1.1 & depth of discharge of 80%. |  | Kindly clarify the Point of Coupling (POC) at which the Round Trip Efficiency (RTE) shall be evaluated, i.e., whether it shall be measured at the 33 kV BESS interface or at the 220 kV Grid POI, as the tender mentions measurement at the POC | Round-trip efficiency of the BESS (RTE) shall be measaured at 33kV BESS Termination Point.
41 | Sub-Section F: O&M Agreement Page 45 of 47 | 2.3 Liquidated Damages: | f the measured usable energy capacity falls below the guaranteed Degradation Curve, the Supplier shall pay the Employer liquidated damages of Rs. 8,000 per kWh for the shortfall in capacity, or at the Employer's option, undertake augmentation/replacement of battery modules at no cost to the Employer to restore the guaranteed capacity within 90 days. |  | The tender specifies a minimum augmentation plan with at least 20% of the awarded capacity distributed over the 15-year O&M period. Kindly clarify whether the year-wise augmentation schedule and quantum in each phase may be proposed by the bidder based on the selected battery technology, degradation characteristics, and performance guarantee, provided the required deliverable capacity is maintained throughout the contract period. This flexibility is requested to optimize augmentation planning and avoid unnecessary over-augmentation in the initial years. | The Tender does not envisage augmentation as the primary means of meeting the required dispatchable energy throughout the contract period. The BESS shall be sized upfront, considering degradation, system losses, and auxiliary consumption, to meet the contractual dispatchable energy requirements. The augmentation provisions specified in the Tender are only an exceptional measure that may be invoked by the Employer if the asset fails to meet the required dispatchable energy commitment. Accordingly, bidders shall not propose augmentation as part of their planned compliance strategy.
42 | General | - | - | - | Bidder is requested to provide the following report for reference during tender stage- 1. Existing Site investigation Report. 2. Existing Topography survey. 3. Existing Geotechnical investigation. 4. Existing layout & drawings of Roads & Drainage for better understanding. | Site Boundary layout has been provided with the tender. Other details are in the scope of the Bidder.
43 | General | - | - | - | No major tree cutting is envisaged in bidder’s scope other than minor site clearance and removal of shrubs, vegetation required for establishment of the Project. Please confirm. | Clearing plant site and transmission line corridor by cutting of trees, bushes and shrubs including disposal of waste material is within the scope of the Bidder. Also, please refer to Amendment No. 5
44 | General | - | - | - | owner to provide Construction Power and Construction Water availability at site to be made to the contractor.kindly confirm | Construction Power and Construction Water shall be in the scope of the Contractor
45 | General | - | - | - | Please confirm if any ground improvement is required at the site. Kindly share the preliminary geotechnical investigation report with expert recommendations of SBC during tender stage. | Assesment of ground improvement requirement shall be a part of the geotechnical investigation,which is in the scope of the Bidder.
46 | General | - | - | - | Please provide the AutoCAD & ,kmz file of the plant with clear boundary demarcations. | Land Acquisition is under process. Enumbrance free land of required area shall be made available for plant deployment. KMZ shall be shared once Land Acquisition is complete.
47 | General | - | - | - | While carrying out construction activities below ground level, if we meet any obstruction e.g. presence of any drainage pipe / water or fire pipeline, any leftover foundation concrete, live wire etc., the owner shall arrange to remove the same & we shall be free by the owner from any such obstruction for conducting our works. Please confirm | Any underground obstruction encountered during execution shall be promptly brought to the notice of the Employer. Removal or relocation of such obstructions, wherever required, shall be carried out by the Contractor only after obtaining the Employer's prior approval and shall be deemed to be within the Contractor's scope of work.
48 | General | - | - | - | We presume that area provided for each unit in the tender document is 100% usable. No any hindrances available at site. Please confirm. | Land Acquisition is under process. Enumbrance free land of required area shall be made available for plant deployment. KMZ shall be shared once Land Acquisition is complete.
49 | General |  |  |  | Kindly clarify the startup philosophy of the BESS during grid outage, prolonged bad weather, or islanding conditions when the battery SOC is low or depleted. In such scenarios, how will the auxiliary power required for BESS startup (including PCS, HVAC, EMS, etc.) be made available? Further, please confirm whether the Solar Inverter/Plant is expected to provide black-start auxiliary power to the BESS, or whether a separate black-start source shall be considered by the bidder. | The startup philosophy shall be finalized by the Successful Bidder during detailed engineering. The BESS shall be provided with Black Start capability in accordance with the Tender Amendment No.6. The Successful Bidder shall provide all necessary PCS, EMS, auxiliary power arrangements, and associated Balance of System (BoS) required to facilitate Black Start operation.
50 | General | - | - |  | Please share the kmz file. or the BESS area coordinates. | Land Acquisition is under process. Enumbrance free land of required area shall be made available for plant deployment. KMZ shall be shared once Land Acquisition is complete. The BESS area shall be finalized by the Successful Bidder during detailed engineering based on the approved plant layout and design.
51 | General Query |  |  |  | Please confirm the short circuit rating to be consider in AC & DC side of PCS. | Shall be finalised during Detailed Engineering
52 | BDS | Clause 45.2 & 45.3, ITB Page 33 | Micro and Small Enterprises (MSEs) registered under Udyam Registration are eligible to avail benefits under the policy. MSEs are exempted from payment of EMD. | Kindly clarify whether Medium Enterprises registered under Udyam Registration are also eligible for EMD exemption. If not, explicitly confirm that exemption is restricted only to Micro and Small Enterprises. | EMD Clarification is required to avoid bid rejection due to differing interpretation of MSME policy. | The provisions of Clause 45 under Section II, "INSTRUCTION TO BIDDERS (ITB)" are self-explanatory and require no further clarification.
53 | ITB | Clause 16, ITB Page 14-15 | EMD to be submitted as prescribed in the tender. | Request acceptance of EMD/BG in the name of Lead Member of JV/Consortium where consortium bidding is permitted. | Common practice in Government EPC tenders and avoids duplication of bid security. | Terms and Conditions of the Tender shall prevail
54 | SCC No. 16 Payment Terms | Advance Payment Clause, Page 177 | Advance payment available against Advance Bank Guarantee | Request SECI to allow Insurance Surety Bond in lieu of Advance Bank Guarantee for release of advance payment. | Reduces non-fund-based banking limits and aligns with Government initiatives promoting Surety Bonds in infrastructure projects. | Terms and Conditions of the Tender shall prevail
55 | Technical Doc part 1 | Clause 1 | The Owner shall deliver PV Modules at the Project site as Free Issue Items. |  | kindly provide the PAN file of module and make | Make and model of PV Module and the PAN file shall be shared with the succesfull bidder during detailed engineering
56 | Technical Doc part 1 | Clause 1 | Point of Interconnection (POI) 220 kV Busbar at the 220/33 kV Plant Pooling Substation |  | Any retrofication/Extention is required or not ? | Extension of the existing busbar is required
57 |  |  | General |  | Are gantry structures available for feeder termination? | Additional gantries for feeder termination shall be constructed by the Contractor
58 |  |  | General |  | Is space available for additional gantry inside substation? | Yes
59 | Technical Doc part 1 | Clause 5.22 | 4 -5 km stretch of existing 220 kV overhead transmission lines from 300 MW Pooling substation, Ramagiri to Pavagada ISTS Substation. |  | Please clarify the transmission line scope, including the start and end points. Kindly confirm whether the bidder's scope includes only the conductor or the complete transmission line, including towers/structures and all associated works, as the SLD does not show the transmission line arrangement. | Only conductor is in the scope of the Bidder. Please refer to Amendment No. 2 and 4
60 | Technical Doc part 1 |  | General |  | Is right of way available for evacuation line or cable route? Or it is in Bidders scope | RoW of evacuation line/cable works envisaged within the SoW of subject tender is within scope of the Bidder
61 | Technical Doc part 1 | Clause 1 | Point of Interconnection (POI) 220 kV Busbar at the 220/33 kV Plant Pooling Substation |  | Bus Fault Level (KA & Sec) where power evacuation to be connected.? | 50 kA per 1 sec. Please refer to Amendment No. 3.
62 | Technical Doc part 1 |  | General |  | Is there any reactive power (VAR) support requirement from BESS? | The Solar + BESS Package shall provide the reactive power support required for the overall 50 MW FDRE Project (comprising the Wind and Solar + BESS Packages), in accordance with the Tender requirements and applicable Grid Code. Compliance shall be assessed at the 220 kV interconnection point at the remote grid substation where the existing 300 MW Solar Power Plant is connected. Grid interconnection studies carried out by the Successful Bidder during detailed engineering shall form the basis for assessing compliance and finalizing the means of achieving the required reactive power support.
63 | Technical Doc part 1 |  | General |  | Are there any harmonic limits (THD%) specified by the utility? And wind SVJ and Harmonics are in solare bidders scope / | The Solar + BESS Package shall provide the reactive power support required for the overall 50 MW FDRE Project (comprising the Wind and Solar + BESS Packages), in accordance with the Tender requirements and applicable Grid Code. Compliance shall be assessed at the 220 kV interconnection point at the remote grid substation where the existing 300 MW Solar Power Plant is connected. Grid interconnection studies carried out by the Successful Bidder during detailed engineering shall form the basis for assessing compliance and finalizing the means of achieving the required reactive power support or installation of Harmonic Filters.
64 | Technical Doc part 1 | Clause 6.33 | Installation of fire detection and fire protection system for buildings/containers, transformer yard and switchyard. |  | Specify for available fire protection system in BESS container | Shall be finalised during Detailed Engineering during approval of Battery Container. Supply, Installation and Commissioning of BESS Containers is in the scope of the Package 1 Contractor.
65 | Technical Doc part 1 |  | General |  | Recommended percentage impedance from PCS vendor for IDT degine | Shall be finalised during Detailed Engineering as per PCS Manufacturer's recommendations. Supply, Installation and Commissioning of BESS PCS is in the scope of the Package 1 Contractor.
66 | Technical Doc part 1 |  | General |  | How many PCS can connect at single LV winding of IDT ? | Shall be finalised during detailed engineering
67 | Technical Doc part 1 |  | General |  | Does PCS support black start functionality? | Please refer to Amendment No. 6
68 | Technical Doc part 1 | Clause 5.25 | Auxiliary supply system including auxiliary transformers, distribution panels, cables, and related accessories for plant internal consumption. |  | What is the source of auxiliary power supply? | The tender envisages that Auxiliary power shall be sourced from the Solar Power Plant during solar generation hours and from the Grid during non-solar hours. During BESS discharge, the auxiliary loads of the BESS shall be supplied from the BESS itself.
69 | Technical Doc part 1 |  | General |  | Is DG backup required for auxiliary loads? | Shall be finalised during detailed engineering
70 | Technical Doc part 1 |  | General |  | What is the availability of water for fire protection system? | Shall be arranged by Contractor
71 | Technical Doc part 1 |  | General |  | Request clarity on availability of construction power and water at site. ? | Shall be arranged by Contractor
72 | Technical Doc part 1 |  | General |  | What is the source of water for Fire protection Systerm (tank capacity / reservoir)? | Shall be finalised during detailed engineering
73 | Technical Doc part 1 |  | General |  | Kindly provide the complete proposed cable routing from the plant to the evacuation point, including trench alignment, route length, turning points, road crossings, cable depth, and any obstructions or right-of-way constraints | Cable routing inclusive of the trench alignment and routing shall be finalised during detailed engineering.
74 | Technical Doc part 1 | Clause 6.33 | Installation of fire detection and fire protection system for buildings/containers, transformer yard and switchyard. |  | Please confirm whether the fire-suppression system is designed to deliver equal and adequate nozzle operating pressure to both BESS containers during a simultaneous fire event | Shall be finalised during detailed engineering
75 | Technical Doc part 1 | Clause 7.3 | It shall mainly comprise of auxiliary transformer, AC distribution board(s) (ACDB), Battery & battery charger system, emergency lighting network, Uninterrupted power supply (UPS), distribution cables and metering & protective devices. |  | Is separate auxiliary metering required for the project? | Yes
76 | Technical Doc part 1 |  | General |  | What is the metering point location for Auxiliary ? | Shall be finalised during detailed engineering
77 | Technical Doc part 1 |  | General |  | Is above-ground cable tray routing permitted? | Yes
78 | Technical Doc part 1 |  | General |  | Are underground cable trenches available between substation and BESS area? | The same shall be proposed during detailed engineering and developed as per approved drawings during the Construction phase by Contractor
79 | Technical Doc part 1 |  |  |  | What is power at POI 50MW or 60MW please confirme | During the Performance Guarantee (PG) Test, the Solar PV Plant shall demonstrate 70 MW AC and the BESS shall demonstrate 25 MW AC at the 220 kV Point of Interconnection (POI). However, during project operation, the scheduled power injection at the 220 kV POI for the overall 50 MW FDRE Project (Wind + Solar + BESS) shall not exceed 50 MW, in accordance with the Tender requirements.
80 | Technical Doc part 2 |  |  |  | What is the rating for Panels for wind ? | Query not understood
81 | Technical Doc part 1 | Clause 5.2 | ABT meters with all necessary metering rated CTs and PTs at the plant take-off point |  | ABT metering is not indicated in the Single Line Diagram (SLD). Kindly clarify the scope of ABT metering, including whether its supply, installation, testing, commissioning, and integration are within the bidder's scope or the owner's scope. | Supply, installation, testing, commissioning, and integration of ABT Meters at the plant take-off point as well as at the transformer bay to be constructed at the existing 300 MW pooling substation are within the bidder's scope.
82 | Technical Doc part 1 |  | General |  | Please Clearfy the OPGW conductor scope . | Not in Bidder's scope
83 | Technical Doc part 1 |  | General |  | Clearfy the Telemetry at existing system | Required signals from the Package 1 equipment shall be interfaced with the existing telemetry system of the 300 MW Solar Power Plant Pooling substation
84 |  | Clause 5.3 | If any ground undulations at column locations are observed the same shall be filled up with PCC (1:3:6) up to surrounding ground level immediately after pile installation before start of erection of other MMS members. |  | Please clarify the permissible ground undulation between adjacent MMS columns. Also confirm the maximum extent of ground dressing/levelling required at each column location after pile installation. | As already clarified in Cl. 5.3 of Section - VII Sub-Section C of Tender that If any ground undulations at column locations are observed the same shall be filled up with PCC (1:3:6) up to surrounding ground level immediately after pile installation before start of erection of other MMS members. In case of pile, the PCC fill shall extend min. 100mm outside pile cap all around and remaining area may be filled up with local soil properly compacted.
85 |  | Clause 6.2 | The Approach road connecting nearest public road and the Main gate shall be of 4.0m wide carriage way with 0.5m wide shoulders on either side. |  | Please confirm Approach road route / Qty. as no nearby public road visible nearby. | Assesment of Approach road requirements is in the scope of the Bidder.
86 |  | Clause 6.9 | Maintenance pathways of min. 1.0m width shall be provided between SPV arrays for easy movement of maintenance staff, tools, equipment and machinery, washing of modules etc. |  | For whole PV Array, levelled compacted pathway required?? | Maintenance pathways of min. 1.0 m width shall be provided.. The pathway area shall be generally levelled and well compacted manually/ mechanically. As per Cl. 6.9 of Section - VII Sub-Section C of Tender.
87 |  | Clause 6.10 | 2.5m wide corridor compacted to a depth of 300mm shall be left along inside of the plant boundary suitably maintained clean of any vegetation and shall be provided with adequate illumination for movement of security personnel. |  | We understand that Only Compacted Pathway/corridor required along periphery of PV Boundary? no additional road is is required. | 2.5m wide corridor compacted to a depth of 300mm shall be provided as per Cl. 6.10 of Section - VII Sub-Section C of Tender.
88 |  | Clause 7.8 | Suitable size plant peripheral drain as per design and requirement (min. 450mm wide x 450mm deep) along inside of plant boundary wall/ fence |  | For Whole PV Area Peripheral drain required? or it shall be as per design. | Suitable size plant peripheral drain as per design and requirement (min. 450mm wide x 450mm deep), however detail shall be finalized during detailed engineering. Terms and condition of tender shall prevail.
89 |  | Clause 8.1 | The plant peripheral boundary shall be provided with chain link fence as per the tender drawing titled ‘Chain link fence Drawing’ attached in Annexure-D |  | Chain link fencing for Provided total Land boundary or for PV Area only. | Chain link fencing shall be provided as per site boundary layout attached "Dwg. Title: Tentative Land Layout (Solar + BESS Package)" on Page 363 of 373 with the Tender.
90 |  |  | General |  | Please confirm Whole Land area Land development and peripheral compacted corridor need to provide or for PV Area only. | Query requires further clarification
91 |  | Clause 10.10.1 | The bidder shall conduct wind tunnel studies for the evaluation of wind loads on PV modules to be adopted for the analysis and design of MMS |  | Bidder proposes to submit structural design calculations along with the STAAD model for MMS design. Kindly confirm that a separate wind tunnel study is not mandatory. | Wind tunnel study is mandatory to evaluate the wind loads on the PV modules for use in the analysis and design of the Module Mounting Structure (MMS). Terms and condition of tender shall prevail.
92 |  | Clause 11.3 | Min. depth of foundation for all buildings and plinth for open installations shall be 1.5 m below NGL. |  | For Hard rock area, Foundation depth shall be 0.5 m below NGL. Please confirm. | Refer to Sl. No. 12 of Amendment
93 |  |  |  |  | Is column Extention Allowed. If yes then Bidder proposes Black metal for the same. | Column Extention is allowed subjected to design verifications during detail engineering. However, the same shall be provided with HDG Coating as per the Tender requirements.
94 |  | Clause 13.7 | Column post coating reference 90 micron minumum. |  | Bidder proposes Column Post Coating 80 micron Minumum HDG.. Kindly confirm | Accepted, Refer Sl. No. 15 of Amendment
95 |  | Clause 13.7 | Purlin Min. thickness shall be 1.2 mm - Table B |  | Bidder roposes purlin thickness shall be 0.9 / 1 mm - HAT Section as per MMS Designing. Pl. confirm | Selection of member section type (Channel/HAT/Z etc.) for purlin members shall be in the scope of the bidder. However, Min. section thickness requirement of 1.2 mm shall prevail.
96 |  | Clause 13.7 | Bracing Min. thickness shall be 2 mm - Table A |  | Bracing thickness shall as per MMS Designing. Pl. confirm. | Terms and condition of tender shall prevail.
97 |  |  |  |  | Bracing can be considered from AL-Zinc Alloy CR Material If yes, Pl. clarify Bracing thickness. | Bracing members of MMS shall have HDG coating as stipulated in the Tender. Terms and condition of tender shall prevail.
98 |  |  |  |  | Bidder proposes Column material with minimum yield strength of 350 MPa and all other MMS members with minimum yield strength of 550 MPa. Kindly confirm acceptance. | Terms and conditions of tender shall prevail.
99 |  |  |  |  | Please confirm whether AZ150 coating can be considered for all cold-formed MMS members. | Terms and conditions of tender shall prevail.
100 |  |  |  |  | Is 20% Wind reduction applicable as per IS 875 Part 3 in MMS Designing? | Wind load shall be assessed as per wind tunnel study results and the same shall be used for MMS design.
101 |  | Clause 17.1 | Min. 40 mm thick floor finish shall be provided for all buildings. |  | Bidder not considering any floor finishing except MCR. kindly confirm. | Floor finish is applicable to all buildings, including the MCR. However, plinths with open installations may be excluded. The terms and conditions of the tender shall prevail.
102 |  | Clause 13.33 | The length of any cold formed section (CFS) generally shall not be more than 5.5 m. |  | Please confirm whether cold-formed sections longer than 5.5 m may be considered | Specified requirements are suggestive. However, this shall be finalized during detailed engineering.
103 |  | Clause 16.2.3.2 | Storage cabin shall be of PEB (Pre-engineered building) type with RCC framed structure up to plinth level with foundations |  | Pl. confirm Storage cabin size. | Contractor shall provide storage cabin having area adequate for storage of plant spares including PV Modules, cables, MMS spares, etc. subject to a min. area of 450 m2.
104 |  | Clause 16.2.4.1 | Contractor shall provide required number of pre-fabricated security cabins at strategic locations & at corners of the plot and 1 nos. security room at Main entry gate. |  | Please confirm the required number and locations of prefabricated security cabins, as the final plot boundary/layout is yet to be finalized. | 1 No. of Security Room shall be provided at the Main Gate. Additionally, watch towers shall be provided as per the provisions under 'Scope of Works - Cl 7.12'.
105 |  |  |  |  | Separate MCR Building need to consider for BESS and PV Plant? | MCR may be kept common for both BESS and PV Plant. However, this shall be finalized during detailed engineering.
106 |  |  |  |  | Bidder requests to provide KMZ file for better understanding of area. | Land Acquisition is under process. Enumbrance free land of required area shall be made available for plant deployment. KMZ shall be shared once Land Acquisition is complete.
107 | Section VII – Sub Section A | Project Particulars | Supply of PV Modules | Kindly provide the approved PV Module manufacturer(s), detailed datasheet, and PAN file | Required for optimization of layout, MMS design. | PV Modules are supplied by the Owner as Free-Issue Items. Bidders shall assume the specified ratings for bid engineering. The final make and PAN files will be shared during detailed engineering with the successful bidder.
108 | Section VII – Sub Section A | Grid Studies | Contractor shall perform Grid Studies. | Kindly provide existing PSS®E model, short circuit levels and network data required for grid studies. | Necessary for accurate system studies and compliance verification. | PSS®E model of the 300 MW Solar Power Plant in Ramagiri, short circuit levels and network data required for grid studies shall be shared with the successful bidder. PSS®E model of the 70 MW Power Plant with 25 MW/50 MWh BESS shall developed by the Bidder.
109 | Section VII – Sub Section A | Scope of Supply | Contractor to integrate with existing 300 MW Plant. | Kindly provide existing plant architecture, interface drawings and communication philosophy for integration. | Essential for estimating integration work. | Existing plant architecture, interface drawings and communication philosophy shall be shared with the successful bidder.
110 | Section VII – Sub Section A | Existing Substation | Extension of existing Pooling Substation. | Kindly provide GA drawings, equipment layout, cable trench drawings and available bay space of the existing 220 kV substation. | Necessary for detailed engineering and quantity estimation. | GA Drawings, equipment layout, cable trench drawings shall be shared with the succesful Bidder. Space required for incoming 220 kV line bay at the 300 MW Solar Power Plant Pooling Substation is confirmed.
111 | TS-Electrical | Connectors | PV Connectors | Kindly confirm whether connectors supplied with Owner-provided modules shall be considered for compatibility. | Required to avoid connector mismatch. | The connectors to be supplied within the scope of the Bidder shall preferably be of the same make as the connectors of the PV Modules. However, any IEC 62852-certified connector may be employed.
112 | TS-Electrical | Inverter | Reactive Power | Kindly specify the exact reactive power operating range to be guaranteed at POI. | Prevents different bidder assumptions. | Reactive power capability within a power factor range of 0.95 lagging to 0.95 leading at the 220 kV POI corresponding to a net active power injection of 50 MW under maximum ambient temperature as per Procedure for assessment of the Design Temperature for RE Plants in compliance to CEA (Technical Standards for Connectivity to the Grid) Regulations issued by CEA
113 | TS-Electrical | Battery & UPS | Battery Technology | Kindly clarify acceptable battery chemistry for UPS (VRLA/Ni-Cd/Lithium-ion). | Uniform costing among bidders. | Terms and Conditions of the Tender shall prevail. Refer Cl 9.3.2 and 10.3
114 | TS-Electrical | Communication System | Communication Protocol | Kindly specify mandatory communication protocols between SCADA, PPC, EMS, BESS and field equipment. | Required for system integration. | Shall be finalised during detailed engineering
115 | TS-Electrical – BESS | BESS General | BESS of 25 MW / 50 MWh | Kindly confirm the minimum usable energy (AC side) to be guaranteed after considering auxiliary consumption and conversion losses. | Required for accurate battery sizing. | The same is given as "Dispatchable BESS Energy" in Section 1 Project Particulars
116 | TS-Electrical – BESS | Battery Technology | Battery specification | Kindly confirm whether LFP shall be the only acceptable battery chemistry or equivalent technologies meeting all performance requirements shall also be acceptable. | Allows fair competition while maintaining performance. | Technical Specifications are chemistry-agnostic. Any chemistry meeting the mentioned performance and type test requirements are acceptable.
117 | TS-Electrical – BESS | Battery Life | Cycle Life | Kindly specify the minimum guaranteed cycle life, operating profile and annual cycling assumptions. | Necessary for battery warranty calculations. | Kindly refer to "Table 1: Supply-Specific Ratings and Requirements" of the Technical Specifications
118 | TS-Electrical – BESS | Ambient Conditions | Battery Operation | Kindly confirm the design ambient temperature to be considered for guaranteed battery performance. | Required for HVAC and thermal design. | Shall be as per maximum ambient temperature of the site
119 | TS-Electrical – BESS | PCS | Reactive Power | Kindly specify whether reactive power capability shall be available at full active power output without battery derating. | Required for PCS sizing. | The Tender does not mandate any specific approach regarding battery derating. The Successful Bidder shall ensure compliance with the specified reactive power requirement at the 220 kV POI corresponding to a net active power injection of 50 MW under the maximum site ambient temperature. The means of achieving this requirement shall be finalized during detailed engineering based on the grid interconnection studies and may include an appropriate combination of PCUs, PCSs, and/or SVGs.
120 | TS-Electrical – BESS | Auxiliary Loads | Auxiliary Consumption | Kindly confirm whether BESS auxiliary consumption shall be excluded while evaluating guaranteed discharge energy. | Avoids different bidder assumptions. | Shall be included
121 | TS-Electrical – BESS | HVAC | Cooling System | Kindly clarify whether redundant HVAC (N+1) is mandatory for each battery container. | Required for equipment sizing. | Redundant HVAC (N+1) is not mandatory under the Tender. The HVAC configuration shall be finalized by the Successful Bidder during detailed engineering based on its design, while ensuring compliance with all Tender requirements.
122 | TS-Electrical – BESS | Fire Protection | Fire Suppression | Kindly specify the approved extinguishing agent and applicable fire protection standard (NFPA/CEA/IS). | Uniform fire protection design. | The fire protection system shall comply with the applicable requirements specified in the Tender. The extinguishing agent and detailed fire protection philosophy shall be proposed by the Successful Bidder during detailed engineering, subject to compliance with the Technical Specifications and the specified type test requirements, including consistency with the type-tested BoM.
123 | TS-Electrical – BESS | Fire Detection | Smoke & Gas Detection | Kindly clarify minimum gas detection sensors and thermal runaway detection philosophy. | Required for OEM selection. | Shall be finalised during detailed engineering
124 | TS-Electrical – EMS | EMS Functional Requirement | EMS Scope | Kindly provide the detailed functional philosophy and control sequence of EMS for all operating modes. | Required for software engineering. | Refer to Annexure to Amendment: SA - D: Operational Philosophy for Forecasting, Scheduling and Dispatch of the 50 MW FDRE Plant
125 | TS-Electrical – EMS | Operating Modes | Charge/Discharge | Kindly specify the priority logic among solar export, battery charging, peak shaving and reactive power support. | Required for EMS programming. | Refer to Annexure to Amendment: SA - D: Operational Philosophy for Forecasting, Scheduling and Dispatch of the 50 MW FDRE Plant
126 | TS-Electrical – EMS | Forecasting | EMS Integration | Kindly clarify whether forecasting software shall be integrated within EMS or may be provided as an independent platform. | Software architecture clarification. | Refer to Annexure to Amendment: SA - D: Operational Philosophy for Forecasting, Scheduling and Dispatch of the 50 MW FDRE Plant
127 | TS-Electrical | Clause 5 – 33 kV Switchgear | Spare feeders. | Kindly clarify the number of future spare feeders to be considered during busbar sizing. | Standardizes design assumptions. | For the main 33 kV pooling switchgear, provision shall be made for three (3) feeders for integration of the Wind Package or 10% spare feeders, whichever is higher. For all other 33 kV switchgear panels, 10% spare feeders shall be provided.
128 | TS-Electrical | Clause 6 – AC Cables | Cable installation. | Kindly provide the design soil thermal resistivity and ambient temperature to be considered for cable derating. | Accurate cable sizing. | Shall be finalised during detailed engineering
129 | TS-Electrical | Clause 10 – Battery & Battery Charger | Battery system. | Kindly confirm the acceptable battery chemistry (VRLA/Ni-Cd/Lithium-ion) for UPS and DC systems. | Uniform commercial evaluation. | Terms and Conditions of the Tender shall prevail. Refer Cl 9.3.2 and 10.3
130 | TS-Electrical | Clause 11 – Earthing | Earthing system. | Kindly specify the maximum permissible overall plant earth resistance and the acceptable value for individual earth pits. | Establishes clear design criteria. | The earthing system shall be designed in accordance with the Tender requirements. The resistance of each SCADA/Electronic earth pit shall be less than 1 Ω. The overall plant and equipment earthing system shall be designed in accordance with IS 3043, IEEE 80-2000, and the Indian Electricity Rules, based on the system fault current and soil resistivity determined from the geotechnical investigation report.
131 | Section VII – TS Electrical | Clause 14 – BESS | 25 MW / 50 MWh Battery Energy Storage System | Kindly clarify whether the specified 50 MWh rating refers to nominal DC battery energy or guaranteed usable AC energy at the Point of Interconnection. | Uniform battery sizing among bidders. | Guaranteed usable AC energy at the Point of Interconnection.
132 | TS-Electrical | Clause 14 | Round Trip Efficiency | Kindly clarify the guaranteed Round Trip Efficiency (RTE) measurement methodology and test conditions. | Avoids different bidder assumptions. | Refer to GA – C Plant Documentation, Commissioning & Test Procedure and GA – H Functional Guarantee Test Procedure
133 | TS-Electrical | Clause 14 | Thermal Runaway | Kindly specify the minimum thermal runaway detection philosophy, gas sensors and automatic isolation sequence. | Safety compliance. | The Tender does not prescribe a specific thermal runaway detection philosophy, gas sensing arrangement, or automatic isolation sequence. The Successful Bidder shall propose a compliant design in accordance with the applicable standards, Tender requirements, and the demonstrated type-tested system. The same shall be reviewed during detailed engineering.
134 | TS-Electrical | Clause 14 | PCS Reactive Power | Kindly confirm whether full reactive power capability shall be available simultaneously with full active power output. | Determines PCS sizing. | The Successful Bidder shall ensure compliance with the specified reactive power requirement at the 220 kV POI corresponding to a net power injection of up to 50 MW under the maximum site ambient temperature. The means of achieving this requirement shall be finalized during detailed engineering based on the grid interconnection studies and may include an appropriate combination of PCUs, PCSs, and/or SVGs.
135 | TS-Electrical | Clause 14 | Black Start | Kindly clarify whether Black Start functionality is mandatory for the BESS. | Impacts EMS and PCS design. | Black Start functionality shall be provided as part of the BESS. The Successful Bidder shall incorporate all necessary provisions in the PCS, EMS, and auxiliary Balance of System (BoS) to enable Black Start operation. Please refer to Amendment No. 6.
136 | TS-Electrical | Clause 19 – Plant Pooling Substation Equipment | Pooling Substation | Kindly provide the fault level, bus configuration, future expansion philosophy and available spare feeder provisions of the pooling substation. | Required for equipment sizing. | Please refer to Scope of Works, SA – B: Indicative Single Line Diagram (SLD) and Amendment No. 3.
137 | TS-Electrical | Project Particulars | Reactive Power Capability | Kindly clarify whether the specified 0.95 lagging to 0.95 leading power factor requirement at the 220 kV POI shall be demonstrated with 50 MW net export only, irrespective of the instantaneous solar generation (70 MWAC) and BESS operating mode. Further, kindly confirm whether reactive power contribution from Solar PCUs, BESS PCS, and SVGs may be combined to meet this requirement. | This clarification is required for proper sizing of inverters, PCS, SVGs, and transformer while ensuring uniform bid assumptions. | The Successful Bidder shall ensure compliance with the specified reactive power requirement at the 220 kV POI corresponding to a net active power injection of 50 MW under the maximum site ambient temperature. The means of achieving this requirement shall be finalized during detailed engineering based on the grid interconnection studies and may include an appropriate combination of PCUs, PCSs, and/or SVGs.
138 | Contractual Document | ITB Page 12 of 52 | Contractor shall mandatorily obtain the registration under GST Law at Central level and/or in respective State as may be required. Further, Contractor shall mandatorily file returns under GST before their due date & comply with the requirements of the Law within timelines. Before releasing the payment to the Contractor. Owner shall not be responsible for any delay in payment release to the contractor in case the GST compliance is not fulfilled from the contractor side in any manner. Contractor shall be responsible to comply with all the requirements of applicable provisions of GST. Contractor has to mandatorily get registered under GST at Central and relevant State(s). Contractor shall file all the returns on timely basis and upload all the Invoices and acceptance thereof as may be required under the provisions of GST. In case, it is found that Owner is not able to take Input Tax Credit (ITC) benefit of the taxes due to any fault of the Contractor, Owner shall be constrained to deduct the amount from the payments to be made to the Contractor or recover the same in any other manner. | As per our understanding of the tender provisions, Solar PV Modules are being supplied separately, while the contractor’s scope primarily comprises the design, engineering, supply, installation, testing, and commissioning (DSITC) of the Balance of System (BoS) components up to the 33 kV pooling point. We also understand that all applicable taxes, duties, levies, and GST pertaining to the contractor’s scope are to be included in the EPC contractor’s quoted price. It has been observed that bidders in similar BoS tenders are adopting different GST treatments, with some considering an effective GST incidence of 8.9% i.e. 70:30 ratios under GST Notification 1/2017 applicable to Solar Power Generating Systems (SPGS), while some of the bidders are quoting GST at 18% as per applicable HSN/ SAC. Such divergence may lead to non-uniform bid evaluation and create ambiguity during contract execution and invoicing. In this regard, we kindly request to assess the applicability of the said provision. However, our query as set below for the seeking of clarity. Whether the BoS package under the subject tender is intended to qualify as part of a Solar Power Generating System (SPGS) for GST purposes and be eligible for the applicable concessional GST i.e. 70:30 ratios under GST Notification 1/2017 or based on HSN / SAC code. Such clarification would ensure consistency in bid evaluation while minimizing the risk of future tax-related disputes. Since the Solar PV Modules are being free-issued by SECI, the guidance on the applicable GST treatment would be beneficial for both SECI and the bidders from a compliance and valuation perspective. Please clarify. |  | Terms and Conditions of the Tender shall prevail
139 |  |  | Project Particulars For Operational Acceptance (RTE Guarantee), Round-trip efficiency of the BESS (RTE) shall be ≥85%, including auxiliary consumption, at 100% rated power at the 33 kV BESS Termination Point. | Dispatchable BESS Energy Requirement The tender specifies 50 MWh dispatchable energy at the 33 kV Point of Interconnection (POI) in the first year, while the project nameplate energy capacity is also specified as 50 MWh. Since system losses (including battery degradation, inverter losses, transformer losses, and auxiliary consumption) must be considered, To achieve 50 MWh dispatchable energy at the POI, the installed BESS nameplate energy capacity would need to be higher than 50 MWh. Kindly clarify whether the specified 50 MWh refers to the installed (nameplate) BESS capacity or the dispatchable energy at the 33 kV POI. |  | 50 MWh is the dispatchable energy at the POI, which is the 220 kV Injection Point
140 |  |  | Project Particulars Round-trip efficiency of the BESS (RTE) shall be ≥85%, including auxiliary consumption, at 100% rated power at the 33 kV BESS Termination Point. | Round-Trip Efficiency (RTE) Requirement: The tender specifies a minimum Round-Trip Efficiency (RTE) of 85%. Based on currently available commercial battery cell technologies and considering the complete BESS (including PCS, transformer, auxiliary loads, and other system losses), achieving a guaranteed system-level RTE of 85% is challenging. Kindly clarify whether an overall BESS RTE in the range of 82%–85% would be considered acceptable, in line with commercially available technologies and current industry standards. |  | Terms and Conditions of the Tender shall prevail
141 |  |  | Project Particulars Solar AC Capacity 70 MW Solar DC Capacity 91 MW Power Transformer Capacity 60MVA | Kindly clarify the adequacy of the specified 33/220 kV, 60 MVA Power Transformer. Since the Solar PV Plant capacity is 70 MW AC, the specified 60 MVA transformer appears insufficient for evacuation of the full plant output. Please confirm whether (i) the export capacity is limited to 60 MVA, (ii) an additional transformer/bay is envisaged under a separate scope, or (iii) the transformer rating should be revised to match the full plant evacuation capacity |  | The specified transformer ratings are adequate for meeting the Tender requirements. The Solar + BESS Package forms part of a 50 MW FDRE Project, and the net power injection at the 220 kV POI shall not exceed 50 MW at any point in time. The excess power over 50 MW shall be employed to charge the BESS. Accordingly, the transformer ratings specified in the Tender have been selected to meet the project requirements.
142 |  |  | Project Particulars For Operational Acceptance (RTE Guarantee), Round-trip efficiency of the BESS (RTE) shall be ≥85%, including auxiliary consumption, at 100% rated power at the 33 kV BESS Termination Point. | Dispatchable BESS Energy Requirement The tender specifies 50 MWh dispatchable energy at the 33 kV Point of Interconnection (POI) in the first year, while the project nameplate energy capacity is also specified as 50 MWh. Since system losses (including battery degradation, inverter losses, transformer losses, and auxiliary consumption) must be considered, To achieve 50 MWh dispatchable energy at the POI, the installed BESS nameplate energy capacity would need to be higher than 50 MWh. Kindly clarify whether the specified 50 MWh refers to the installed (nameplate) BESS capacity or the dispatchable energy at the 33 kV POI. |  | 50 MWh is the dispatchable energy at the POI, which is the 220 kV Injection Point
143 |  |  | Project Particulars Round-trip efficiency of the BESS (RTE) shall be ≥85%, including auxiliary consumption, at 100% rated power at the 33 kV BESS Termination Point. | Round-Trip Efficiency (RTE) Requirement: The tender specifies a minimum Round-Trip Efficiency (RTE) of 85%. Based on currently available commercial battery cell technologies and considering the complete BESS (including PCS, transformer, auxiliary loads, and other system losses), achieving a guaranteed system-level RTE of 85% is challenging. Kindly clarify whether an overall BESS RTE in the range of 82%–85% would be considered acceptable, in line with commercially available technologies and current industry standards. |  | Terms and Conditions of the Tender shall prevail
144 | Technical Document Part-1 (Sub-Section A – Scope of Work) | Scope of Work / Site Information | The project shall be executed at Ramagiri, Sri Sathya Sai District, Andhra Pradesh. The Contractor shall execute all works including internal infrastructure and shall obtain ROW, permits and approvals for the 33 kV overhead transmission line/underground cable wherever applicable. | Kindly confirm whether the entire project land required for the Solar PV Plant, BESS, internal roads, pooling substation, switchyard, transmission line corridor, and all associated facilities is already in the physical possession of SECI and will be handed over to the successful bidder free from all encumbrances. Further, kindly clarify whether all statutory land approvals, Right of Way (ROW), and approach roads are available under the Owner's scope. In case any ROW or statutory permission is required from Government authorities or private landowners for the transmission line or associated works, kindly specify the exact scope and responsibility of the EPC Contractor and confirm whether SECI will provide necessary assistance in obtaining such approvals. | Required for proper assessment of project execution risk and cost estimation. | Land Acquisition is under process. Enumbrance free land of required area shall be made available for plant deployment. KMZ shall be shared once Land Acquisition is complete. All statutory land approvals, Right of Way (ROW), and approach roads are under the Contractor's scope
145 | Technical Document Part-1 – Project Particulars / BESS Performance Requirements | Round Trip Efficiency (RTE) | Round-trip efficiency of the BESS (RTE) shall be ? 85%, including auxiliary consumption at 100% rated power at 33 kV BESS Termination Point. | Kindly clarify the methodology for determination of Round Trip Efficiency (RTE), including (i) charging and discharging duration, (ii) initial and final State of Charge (SOC), (iii) ambient temperature conditions during testing, (iv) inclusion/exclusion of HVAC, fire protection, lighting, auxiliary transformers, PCS standby consumption and other auxiliary loads, (v) measurement points for import and export energy, and (vi) whether the RTE requirement shall be applicable at Beginning of Life (BOL) or throughout the O&M period considering battery degradation. Kindly also confirm the acceptance test procedure and permissible measurement tolerance. | Required for uniform interpretation of performance guarantee and accurate BESS sizing. | Methodology for determination of RTE is given in GA – H Functional Guarantee Test Procedure. In this regard: (i) The BESS shall be charged to its full available energy level at rated charging power and discharged at the rated power to its minimum available energy level, in accordance with the FG Test Procedure; (ii) The initial and final State of Charge (SoC) shall correspond to the full and minimum SoC levels, respectively, as per the approved BESS operating philosophy; (iii) The RTE test shall be conducted under the prevailing site ambient conditions after stabilization of the HVAC system; (iv) The guaranteed RTE shall include all auxiliary consumption associated with the BESS; (v) RTE shall be determined based on energy measurements at the specified BESS Point of Coupling (33 kV Termination point). Wherever auxiliary loads are supplied from an external source, the corresponding auxiliary energy shall be accounted for in accordance with the measurement methodology specified in the FG Test Procedure. Measurement point will be suitably identified within the Bidder's design.; (vi) The RTE guarantee of ≥85% is applicable during the Performance Guarantee/Functional Guarantee Test for Operational Acceptance. During the O&M period, performance shall be evaluated based on the contractual availability and dispatchable energy requirements specified in the Tender, and not by periodic verification of RTE.
146 | BESS Technical Specifications | RTE Requirement | RTE ? 85% at 33 kV BESS Termination Point. | Kindly confirm whether the minimum RTE of 85% shall be demonstrated at Commissioning (BOL) only. Considering natural battery degradation over the project life, bidders request that compliance be evaluated at Commissioning/Beginning of Life (BOL) and not during the entire O&M period. | Long-term RTE cannot remain constant due to battery ageing. | The RTE guarantee of ≥85% is applicable during the Performance Guarantee/Functional Guarantee Test for Operational Acceptance. During the O&M period, performance shall be evaluated based on the contractual availability and dispatchable energy requirements specified in the Tender, and not by periodic verification of RTE.
147 | Technical Document Part-1 | Procurement & Supply – 33 kV Transmission Line | Contractor shall provide 33 kV Overhead Transmission Line/Underground Cable including ROW, permits and approvals. | Kindly provide the finalized transmission line route map, alignment drawing, tower schedule and route survey report for the proposed 33 kV transmission line. | Required for accurate BOQ and engineering. | Shall be finalised during detailed engineering
148 | Technical Document Part-1 | Transmission Line | 33 kV OHTL/UG Cable is in Contractor's scope. | Kindly confirm the approximate route length, break-up of Overhead Line and Underground Cable portions, and whether any route deviation is permitted during detailed engineering. | Scope clarification. | Shall be finalised during detailed engineering
149 | Technical Document Part-1 | BESS Technical Specification | Minimum Battery Container Capacity: 5 MWh | Kindly clarify whether Battery Energy Storage System (BESS) containers with capacities higher than 5 MWh (e.g., 5.5 MWh, 6.0 MWh, 6.25 MWh or higher) shall be acceptable, provided the overall BESS rating of 25 MW/50 MWh, performance guarantees, safety requirements, availability, Round Trip Efficiency (RTE), and all other technical specifications are fully complied with. Further, please confirm that bidders are permitted to optimize the number of battery containers based on their offered technology without affecting the guaranteed system performance. | Required to allow technology-neutral design optimization and encourage adoption of latest-generation battery container technologies. | Bidders are free to optimize the BESS configuration, including the individual container capacity and the number of battery containers, provided the offered system complies with all Tender requirements, applicable regulations, and the guaranteed type test, performance, safety and availability requirements. The final BESS design shall be submitted during detailed engineering for the Employer's review and approval.
151 | Technical Document Part-1 | 1.project Particulars | Power Transformer capacity 60MVA | Since this is 70MW Solar project along with the BESS in this condition the 60MVA Power transformer is enough at Solar Power plant end . Kindly confirm | Understand the rating of the Power Transformer at Solar Power Plant end | The specified transformer ratings are adequate for meeting the Tender requirements. The Solar + BESS Package forms part of a 50 MW FDRE Project, and the net power injection at the 220 kV POI shall not exceed 50 MW at any point in time. The excess power over 50 MW shall be employed to charge theBESS. Accordingly, the transformer ratings specified in the Tender have been selected to meet the project requirements.