## Pre Bid Queries
Balance of System Tender for Setting up of grid connected 700 MW Ground mounted Solar PV plant at Radhanesda, Gujarat
Tender No :SECI/C&P/OP/11/023/2025-26
Sl. No. | Tender Section | Page No. | Clause No | Description as per Tender Document | Queries | Category (Finance/Technical/Contractual) | Clarifications
1 | Technical Tender Document | 31/341 | 2.8.7 | DC cables from SMB to PCU shall be laid over ground by the following methods towards the SMB/String Inverter. (i) Galvanized Iron (GI) or Fiber Reinforced Plastic (FRP) cable trays supported on RCC (Reinforced Cement Concrete) ballasts (ii) Galvanized Iron (GI) or Fiber Reinforced Plastic (FRP) cable trays supported on piles (iii) RCC ballasts with split pipe sections at support points In case method (iii) is employed, where the cable span is not fully enclosed in the pipe, care shall be taken to ensure adequate span to prevent cable abrasion against the concrete surface and vertical clearance from the ground as defined elsewhere in this technical specifications. Exposed surfaces of concrete structures shall be painted with chemically resistant, coal tar-extended epoxy coating system. To safeguard steel components, hot dipped galvanisation of minimum 110 microns thickness shall be provided. | The Bidder requests confirmation on whether alternative above-ground Cable laying methodologies, other than the three methods specified in the amendment / pre-bid clarification, would be acceptable, provided such alternatives meet the technical and durability requirements. | Technical | Please refer S.No.4 of Amendment-2.
2 | Technical Tender Document | 19/341 | 6.22 | Construction of dry type robotic cleaning systems and wet type module cleaning systems. As part of the Wet Cleaning System, Water Storage Tank of 33 Lakh Litres, Supply pipes & Pump shall be constructed to cater to water supply for module cleaning, day-to-day requirement of drinking water and other needs of SPV power plant during entire O&M period. As part of the dry type Cleaning System, the Contractor shall provide semi-autonomous/autonomous type robotic cleaning systems as per detailed specifications. | The scope currently envisages both wet-type and dry-type module cleaning systems along with associated permanent water storage and pumping infrastructure. We wish to highlight that provisioning and maintaining full-fledged infrastructure for both systems would result in significant capital cost, while the actual utilization of wet-cleaning facilities is expected to be limited, as wet cleaning is typically required only once per month during the dry season. In view of the above, we suggest that instead of installing permanent wet-cleaning infrastructure (including large-capacity water storage tanks, pumping systems, and pipelines), the monthly wet-cleaning requirement may be met through a manual wet-cleaning methodology, while regular and frequent cleaning is carried out using dry-type robotic cleaning systems. This approach would ensure effective module cleanliness and energy generation while optimizing project cost and asset utilization. Further, to ensure uniformity in design philosophy and compliance with the intended generation performance, we request SECI to kindly define the minimum requirement and ratio of semi-autonomous and fully autonomous robotic cleaning systems to be deployed for the project. | Technical | The terms and conditions of the tender document shall prevail.
3 | Sl. No 164 of Prebid Queries response |  |  | While the bund height is varying for different stretches of the peripheral bund, the road topping over the bund (175 THK GSB + 150 THK DBM) is same for the entire stretch. The construction of the peripheral bund as per the provided details shall be in the scope of the bidder. | As per typical cross section provided by client, the top layer of road in bund is 150mm WBM whereas in PBQ clarification sheet it is mentioned as 150mm DBM layer. Bidder proposes 150mm WBM layer as per cross section provided. | Technical | Section details shall be followed as per 'Specific Annexure C: Bund Layout & Details' drawing shared with Amendment - 01. Side slope shall be 1V:2H.
4 | Technical Tender Document | 7/341 |  | Plant End Substation Switching Scheme (220 kV) :Double Bus Scheme with Bypass-Isolator (Main Bus-I & Main Bus-II/Transfer Bus) Refer Specific Annexure – B: (Indicative Pooling Substation SLD) | Bidder seeks to consider double main bus without bypass isolator. | Technical | The terms and conditions of the tender document shall prevail.
5 | Technical Tender Document | 270/341 | 7.1 | Liquidated damages (LD) of amount equal to the NPV of the estimated shortfall in cash flow resulting over the period of 25 years due to shortfall in actual generation against target generation, calculated at a tariff of Rs. 2.45 per unit (kWh) and discount rate of 6.7% shall be levied. | The Bidder requests SECI to exclude/remove the applicability of Liquidated Damages (LD) related to generation shortfall during the OTGT period. OTGT is intended as a performance evaluation and stabilization phase, and hence imposition of long-term generation-linked LD during this stage may not be appropriate. Generation-linked LD, if any, may instead be made applicable during the O&M period, as defined in the Contract. | Technical | The terms and conditions of the tender document shall prevail.

## Amendment-2
Balance of System Tender for Setting up of grid connected 700 MW Ground mounted Solar PV plant at Radhanesda, Gujarat
Tender No :SECI/C&P/OP/11/023/2025-26
S. No. | Section | Page No. | Clause | Original Version | Amendment
1 | Section-VI Sample Forms & Formats | 22 of 85 |  | Form F-12 (DECLATION REGARDING THE MANDATORY PROCUREMENT OF INVERTERS FROM CLASS I LOCAL SUPPLIERS) | Attached as Annexure-1.
2 | Section-VII Sub-section A Scope of Works | 3 of 22 | 1 | Origin of Supply Items - As per MNRE Order on Public Procurement (Preference to Make in India) to provide for Purchase Preference (linked with local content) in respect of RE Sector dated 9th February, 2021 and subsequent amendments | Origin of Supply Items - As per MNRE Order on Public Procurement (Preference to Make in India) to provide for Purchase Preference (linked with local content) in respect of RE Sector dated 9th February, 2021 and subsequent amendments SECI has requested MNRE to waive off the requirement of Class-I local supplier for inverters. Since SECI's request is under consideration, the Bidder shall quote considering inverter supply from Class-I local suppliers. In case SECI gets a waiver after bid submission, the BoS Contractor need not to supply inverters from Class-I local suppliers and subsequently, the contract price will be reduced at the rate of Rs. 3,94,500/per MW plus applicable taxes for the total inverter capacity supplied by the BoS Contractor.
3 | Section-VII Sub-section B Technical Specifications - Electrical | 6 of 85 | 2.8.4 | Solar cables or group of solar cables combined through branch connector shall be laid over ground by the following methods towards the SMB/String Inverter. (i) Galvanized Iron (GI) or Fiber Reinforced Plastic (FRP) cable trays supported on RCC (Reinforced Cement Concrete) ballasts (ii) Galvanized Iron (GI) or Fiber Reinforced Plastic (FRP) cable trays supported on piles (iii) RCC ballasts with split pipe sections at support points for cable protection In case method (iii) is employed, where the cable span is not fully enclosed in the pipe, care shall be taken to ensure adequate span to prevent cable abrasion against the concrete surface and vertical clearance from the ground as defined elsewhere in this technical specifications. Solar cable terminations shall be made with connectors complying IS 16781 / IEC 62852. The connectors shall have degree of protection of IP 68. Exposed surfaces of concrete structures shall be painted with chemically resistant, coal tar-extended epoxy coating system. To safeguard steel components, hot dipped galvanisation of minimum 110 microns thickness shall be provided. | Solar cables or group of solar cables combined through branch connector shall be laid over ground by the following methods towards the SMB/String Inverter. (i) Galvanized Iron (GI) or Fiber Reinforced Plastic (FRP) cable trays supported on RCC (Reinforced Cement Concrete) ballasts (ii) Galvanized Iron (GI) or Fiber Reinforced Plastic (FRP) cable trays supported on piles (iii) RCC ballasts with split pipe sections at support points for cable protection In case method (iii) is employed, where the cable span is not fully enclosed in the pipe, care shall be taken to ensure adequate span to prevent cable abrasion against the concrete surface and vertical clearance from the ground as defined elsewhere in this technical specifications. The Contractor may propose anyother suitable cable routing arrangement provided that it ensures adequate clearance above the High Flood Level (HFL), as specified elsewhere in this Technical Specification, and meets the project’s design, safety, reliability, and statutory requirements for the entire project life. The proposed arrangement shall comply with all applicable codes, standards, and regulations, and shall be subject to review and approval during the Detailed Engineering stage. Solar cable terminations shall be made with connectors complying IS 16781 / IEC 62852. The connectors shall have degree of protection of IP 68. Exposed surfaces of concrete structures shall be painted with chemically resistant, coal tar-extended epoxy coating system. To safeguard steel components, hot dipped galvanisation of minimum 110 microns thickness shall be provided.
4 | Section-VII Sub-section B Technical Specifications - Electrical | 6 of 85 | 2.8.7 | DC cables from SMB to PCU shall be laid over ground by the following methods towards the SMB/String Inverter. (i) Galvanized Iron (GI) or Fiber Reinforced Plastic (FRP) cable trays supported on RCC (Reinforced Cement Concrete) ballasts (ii) Galvanized Iron (GI) or Fiber Reinforced Plastic (FRP) cable trays supported on piles (iii) RCC ballasts with split pipe sections at support points In case method (iii) is employed, where the cable span is not fully enclosed in the pipe, care shall be taken to ensure adequate span to prevent cable abrasion against the concrete surface and vertical clearance from the ground as defined elsewhere in this technical specifications. Exposed surfaces of concrete structures shall be painted with chemically resistant, coal tar-extended epoxy coating system. To safeguard steel components, hot dipped galvanisation of minimum 110 microns thickness shall be provided. | DC cables from SMB to PCU shall be laid over ground by the following methods towards the SMB/String Inverter. (i) Galvanized Iron (GI) or Fiber Reinforced Plastic (FRP) cable trays supported on RCC (Reinforced Cement Concrete) ballasts (ii) Galvanized Iron (GI) or Fiber Reinforced Plastic (FRP) cable trays supported on piles (iii) RCC ballasts with split pipe sections at support points In case method (iii) is employed, where the cable span is not fully enclosed in the pipe, care shall be taken to ensure adequate span to prevent cable abrasion against the concrete surface and vertical clearance from the ground as defined elsewhere in this technical specifications. The Contractor may propose anyother suitable cable routing arrangement provided that it ensures adequate clearance above the High Flood Level (HFL), as specified elsewhere in this Technical Specification, and meets the project’s design, safety, reliability, and statutory requirements for the entire project life. The proposed arrangement shall comply with all applicable codes, standards, and regulations, and shall be subject to review and approval during the Detailed Engineering stage. Exposed surfaces of concrete structures shall be painted with chemically resistant, coal tar-extended epoxy coating system. To safeguard steel components, hot dipped galvanisation of minimum 110 microns thickness shall be provided.
5 | Section-VII Sub-section B Technical Specifications - Electrical | 7 of 85 | 3.2.1 | The Inverter Supplier shall be Class-I local supplier as per MNRE Order on Public Procurement (Preference to Make in India) to provide for Purchase Preference (linked with local content) in respect of Renewable Energy (RE) Sector dated 9th February, 2021 and subsequent amendments. | The Inverter Supplier shall be Class-I local supplier as per MNRE Order on Public Procurement (Preference to Make in India) to provide for Purchase Preference (linked with local content) in respect of Renewable Energy (RE) Sector dated 9th February, 2021 and subsequent amendments. SECI has requested MNRE to waive off the requirement of Class-I local supplier for inverters. Since SECI's request is under consideration, the Bidder shall quote considering inverter supply from Class-I local suppliers. In case SECI gets a waiver after bid submission, the BoS Contractor need not to supply inverters from Class-I local suppliers and subsequently, the contract price will be reduced at the rate of Rs. 3,94,500/per MW plus applicable taxes for the total inverter capacity supplied by the BoS Contractor.
6 | SA-B | 7 of 10 | - | New Clause | 8. Bifacial System i. Use Unlimited sheds 2D-model ii. Ground Albedo- iii. Shade transparent fraction - 0% iv. Structure Shading factor - 5% v. Mismatch loss factor - 10% vi. Height above the ground- Weighted average Module clearance above ground as per Civil Design vii. Bifaciality factor - As per module offered by Owner (Minimum 0.7)
7 | Section I Invitation for Bids | 6 of 10 | 16 | 16.0 Public Procurement Policy - Wrt. Ministry of New & Renewable Energy (MNRE) Order No 283/22/2019-Grid Solar Dated 23rd Sep 2020 for the Public Procurement (Preference to Make In India) including any amendments thereto, so as to Provide Purchase Preference (linked with local content) with respect to Renewable Energy (RE) Sector & Department for Promotion of Industry and Internal Trade (DPIIT) Notification No. P-45021/2/2017-PP (BE-LI) dated 4th June, 2020 including any amendments, the procurement of Solar Modules for the subject tender will be supplied through Class I Local Suppliers only. A Class-I local supplier' means a Supplier or Service Provider, whose Goods, Services or works offered for Procurement, has local content equal to or more than 50%, as defined under the above said orders. | 16.0 Public Procurement Policy - Wrt. Ministry of New & Renewable Energy (MNRE) Order No 283/22/2019-Grid Solar Dated 23rd Sep 2020 for the Public Procurement (Preference to Make In India) including any amendments thereto, so as to Provide Purchase Preference (linked with local content) with respect to Renewable Energy (RE) Sector & Department for Promotion of Industry and Internal Trade (DPIIT) Notification No. P-45021/2/2017-PP (BE-LI) dated 4th June, 2020 including any amendments, the procurement of Solar Modules for the subject tender will be supplied through Class I Local Suppliers only. A Class-I local supplier' means a Supplier or Service Provider, whose Goods, Services or works offered for Procurement, has local content equal to or more than 50%, as defined under the above said orders. SECI has requested MNRE to waive off the requirement of Class-I local supplier for inverters. Since SECI's request is under consideration, the Bidder shall quote considering inverter supply from Class-I local suppliers. In case SECI gets a waiver after bid submission, the BoS Contractor need not to supply inverters from Class-I local suppliers and subsequently, the contract price will be reduced at the rate of Rs. 3,94,500/per MW plus applicable taxes for the total inverter capacity supplied by the BoS Contractor. Such correction in the final Contract Value of the BoS Contract may so happen mid-course or during the Final Closure of the project.
Note on G9: Muthuraj R: Rs. per MW shall be filled.