## Amendment-1
Tender No : SECI/C&P/OP/11/021/2025-26
Tender for “The Manufacturing, Testing, Packing and Forwarding, Supply and Transportation of 870 MWp domestically manufactured Solar PV Modules with domestically manufactured Solar Cells”
S. No. | Section | Page No. | Clause | Original Version | Amendment
1 | Sample Forms and Formats (SFF) | 43 of 66 | Form - 17 | DECLARATION RESTRICTION ON PROCUREMENT FROM CERTAIN COUNTRIES. | Kindly refer to the updated format attached as Annexure A to the Amendment 01.
2 | SECTION – VII SCOPE OF SUPPLY & TECHNICAL SPECIFICATIONS | 230 of 258 |  | Form T01 | Additional Entry in Form T01: 16. Bifaciality factor Updated format attached as Annexure B to the Amendment 01.
3 | SECTION – VII SCOPE OF SUPPLY & TECHNICAL SPECIFICATIONS, PART A | 232 of 258 | 1.4 | 1.4 The Bidder shall offer only one type of PV Module with same Dimensions as per the specifications provided herein. The PV Module dimensions shall not change from the Guaranteed Technical Particular Datasheet (Form: T-01) provided with the bid. | 1.4 The Bidder shall offer only one type of PV Module with same Dimensions as per the specifications provided herein. Not more than 3 wattages within a single module type/family shall be proposed. The PV Module dimensions shall not change from the Guaranteed Technical Particular Datasheet (Form: T-01) provided with the bid.
4 | SECTION – VII SCOPE OF SUPPLY & TECHNICAL SPECIFICATIONS, PART B | 234 of 258 | 1.3 | PV Modules to be supplied under this Contract shall be suitable for use with semi-automatic/fully automatic robotic cleaning systems to be provided under the scope of the Owner / BoS Contractor selected by Owner. The Supplier shall certify that the modules (including glass, frame, and laminate, etc.) are robust against repetitive loads arising from robotic cleaning operations, and shall furnish supporting documents and/or third-party test reports demonstrating durability and compatibility for such cleaning systems prior to supply. | PV Modules to be supplied under this Contract shall be suitable for use with semi-automatic/fully automatic robotic cleaning systems to be provided under the scope of the Owner / BoS Contractor selected by Owner. The Supplier shall certify that the modules (including glass, frame, and laminate, etc.) are robust against repetitive loads arising from robotic cleaning operations and are compatible for such cleaning systems prior to supply.
5 | SECTION – VII SCOPE OF SUPPLY & TECHNICAL SPECIFICATIONS, PART B | 235 of 258 | 2.1 | Additional Entry
6 | SECTION – VII SCOPE OF SUPPLY & TECHNICAL SPECIFICATIONS | 235 of 258 | 3 | Additional Entry | Additional Parameter: Bifaciality Factor: 0.70 (minimum)
7 | SECTION – VII SCOPE OF SUPPLY & TECHNICAL SPECIFICATIONS PART – C: PRE-DISPATCH INSPECTION PROTOCOL | 244 of 258 | 9 | Re-inspection and review In case of minor non-conformities like cleaning issues, label mismatch, etc. which can be easily reworked, Supplier shall rework/replace the modules and offer them for re-inspection to inspector(s). | Re-inspection and review In case of minor non-conformities like cleaning issues, label mismatch, missing sealant. which can be easily reworked, Supplier shall rework/replace the modules and offer them for re-inspection to inspector(s) as per Clause 6(i).
8 | SECTION – VII SPECIFIC ANNEXURE – A: BID EVALUATION CRITERIA | 250 of 258 |  | SECTION – VII SPECIFIC ANNEXURE – A: BID EVALUATION CRITERIA | Updated Annexure - SECTION – VII SPECIFIC ANNEXURE – A: BID EVALUATION CRITERIA Attached as Annexure C to the Amendment 01. Same shall be used to refer the illustration shown under the ITB section of the tender document (clause 31.4 - Evaluation Criteria)

## Pre Bid Queries
Tender for “The Manufacturing, Testing, Packing and Forwarding, Supply and Transportation of 870 MWp domestically manufactured Solar PV Modules with domestically manufactured Solar Cells”
Tender No : SECI/C&P/OP/11/021/2025-26
Sl. No. | Tender Section | Page No. | Clause No | Description as per Tender Document | Queries | Category (Technical/Contractual) | Clarifications
1 | IV | 29 | 47 | The Engineer-in-Charge/Project Manager will have full power and authority to inspect the Supply at any time wherever in progress either on the Site or at the Supplier's premises/ workshops | Kindly reframe the Phrase as, " The Engineer-in-Charge/Project Manager will have full power and authority to inspect the Supply at the Supplier's premises/ workshops" | Contractual | The terms and conditions of the tender document shall prevail. However, inspection of Module whenever carries out a site will be a tri-party inspection by SECI, BoS Contractor and Module Supplier.
2 | IV | 32 | 53.2.9 | If the Supplier fails to commence the work necessary to remedy such defect or any damage to the Facilities caused by such defect within a reasonable time (which shall in no event be considered to be less than seven (7) days), the Owner may, following a notice to the Supplier, proceed to do such work, and the costs incurred by the Owner in connection therewith shall be paid to the Owner by the Supplier or may be deducted by the Owner from any monies due to the Supplier, without prejudice to other rights, which the Owner may have against the Supplier in respect of such defects. | Kindly add, "provided, the cost of the repair does not exceed the price of modules" | Contractual | All such events will be dealth on case to case basis considering the merit of the case and accordingly appropriate decisions will be taken.
3 | IV | 33 | 54 | In case, Supplier shall fail to do so, the Owner may take, at the cost of the Supplier, such steps as may take in all circumstances, be reasonable to make good such defects. The expenditure so incurred by the Owner will be recovered from the amount due to the Supplier. | Kindly add 'provided, the cost of the repair does not exceed the price of modules' | Contractual | All such events will be dealth on case to case basis considering the merit of the case and accordingly appropriate decisions will be taken.
4 | IV | 33 | 55 | If any defect be not remedied within a reasonable time, the Owner may proceed to do the Supply at Supplier's risk and expense and deduct from the final bill such amount as may be decided by the Owner. | Kindly add, "provided, the cost of the repair does not exceed the price of modules" | Contractual | All such events will be dealth on case to case basis considering the merit of the case and accordingly appropriate decisions will be taken.
5 | IV | 33 | 58 | In case the Supplier fails to do so, Owner may on giving the Supplier 07 (Seven) day notice in writing of his intentions to do so, proceed to remove the portion of the Supply so complained of and at the cost of Supplier's, perform all such supply or furnish all such equipment’s provided that nothing in the clause shall be deemed to deprive the Owner of or affect any rights under the Contract, the Owner may otherwise have in respect of such defects and deficiencies. | Kindly add, "provided, the cost of the repair does not exceed the price of modules" | Contractual | All such events will be dealth on case to case basis considering the merit of the case and accordingly appropriate decisions will be taken.
6 | VII | 3 | 1.1 | However, the Supplier shall depute an authorized representative to the site commencing from the date of delivery of first consignment till the completion of all Supplies under this Contract for verification of receipt of the consignment in good condition, and to facilitate the handing over of the same to the Employer/Employer's assignee. | Kindly remove this phrase, as we provide unloading manual & Installation manual. | Technical | Terms and Conditions of the Tender shall prevail
7 | VII | 5 | 1.3 | PV Modules to be supplied under this Contract shall be suitable for use with semi-automatic/fully automatic robotic cleaning systems to be provided under the scope of the Owner / BoS Contractor selected by Owner. The Supplier shall certify that the modules (including glass, frame, and laminate, etc.) are robust against repetitive loads arising from robotic cleaning operations, and shall furnish supporting documents and/or third-party test reports demonstrating durability and compatibility for such cleaning systems prior to supply. | Owner to provide test standard or required tests & test sequences for the finalized robotic cleaning equipment, for conforming its compatibility with PV modules. Owner needs to arrange the required robotic cleaning equipment and accessories for performing the tests. | Technical | Compatibility testing and certification of the PV modules with the proposed robotic cleaning system is outside the scope of this tender and shall be the responsibility of the Owner's BoS Contractor. The impact of cleaning brush and microfiber on module coatings shall be demonstrated through third-party testing in accordance with applicable standards. The module supplier shall not be required to arrange or conduct compatibility testing as part of this procurement, but shall facilitate the process by providing required technical inputs, sample modules, and any other documentation necessary to support the BoS Contractor's compatibility testing, after finalisation of the robotic cleaning system. A compatibility approval letter from the module manufacturer shall be provided at that stage for Owner's review. Refer Amendment No. 4.
8 | VII | 5 | 1.4 | PV Modules supplied under this Contract shall be suitable for deployment on Horizontal Single Axis Tracking (HSAT) systems (1P configuration). Module supplier shall confirm that use of the modules on HSAT systems does not void performance warranty or product warranty obligations. | Owner to provide test standard or required tests & test sequences for the finalized Tracking System, for conforming its compatibility with PV modules. Owner needs to arrange the required Tracking System and accessories for performing the tests. | Technical | Compatibility testing and certification of the PV modules with the proposed tracker system is outside the scope of this tender and shall be the responsibility of the Owner's BoS Contractor. The module supplier shall confirm, at the time of detailed engineering, that their modules are compatible with standard external, internal, and edge mounting/fastening methods. The module supplier shall not be required to arrange or conduct tracker compatibility testing as part of this procurement, but shall facilitate the process by providing required technical inputs, sample modules, mounting specifications, and any other documentation necessary to support the BoS Contractor's compatibility testing, after finalisation of the tracker system. A compatibility approval letter from the module manufacturer shall be provided at that stage for Owner's review.
9 | VII | 6 | 3 | Dimensions Width: 1134 ± 2 | Please update the Width requirement = 1134 -3/+2 | Technical | Terms and Conditions of the Tender shall prevail
10 | VII | 7 | 3 | Holes Position Design Load Requirement (across the length of module) (IS 14286: Part 1) 400 mm 1400 Pa 790 mm 1700 Pa 1400 mm 2000 Pa | Kindly consider the following Load requirements Holes Position Design Load Requirement (across the length of module) 400 mm 1000 Pa 790 mm 1400 Pa 1400 mm 1600 Pa | Technical | Terms and Conditions of the Tender shall prevail
11 | VII | 8 | 4.6 | RFID Tag The database shall include the following details: (iii) Type of cell | Please remove this Phrase, as it is not a mandatory requirement for RFID Tag database as per MNRE | Technical | The same is a requirement of the CPSU scheme. Terms and Conditions of the Tender shall prevail
12 | VII | 10 | 6 | The Supplier shall provide Guaranteed Technical Particular (GTP) datasheet and Bill of Materials (BOM) of the module that is submitted for approval along with the datasheets of each component. | Kindly remove the phrase "along with the datasheets of each component", as we can provide COC (Certificate of Conformity) at the time of Pre-dispatch Inspection | Technical | Terms and Conditions of the Tender shall prevail
13 | VII | 10 | 7.3 | For crystalline-Si modules current binning of modules shall be employed so that Maximum Power current (Imp) mismatch of modules in a bin does not exceed 200 mA. A bin identification methodology shall be employed by the manufacturer (e.g. different colour codes/Identification labels like I2/I3 etc.) on the modules as well as pallet for identification of different bins. The Supplier shall submit the binning scheme to the Employer for approval, | Kindly update, "Current Bin sorting @Impp 0.15A and maintain 2 Current bin I1 & I2. I1 is closed bin & I2 is open." We have current bin printed on module back label as well as in the packing slip also which is pasted over pallet. So there will be no separate requirements of different colour codes/identification labels on the modules as well as pallet for identification of different bins. | Technical | Terms and Conditions of the Tender shall prevail
14 | VII | 11 | 7.5 | Proof of procurement of components as per the approved BOM mentioning manufacturer name, manufacturing date and relevant test certificate shall be submitted during material inspection for verification. | same as Query no.13 , Please remove the phrase "relevant test certificate" | Technical | Terms and Conditions of the Tender shall prevail
15 | VII | 14 | 8.1 | All modules selected for sampling inspection will be re-tested in the sun-simulator. A Pmax retest (repeatability test) variation of ± 2 % on flash Pmax (Production value) will be acceptable | Kindly update- replace '(Production value)' to '(Nominal Power value)' | Technical | Terms and Conditions of the Tender shall prevail
16 | V | 2 | 3.4 | Supplies at site (D + 120 to D + 360 days) | We note that the delivery schedule in the tender specifies supplies at site between D + 120 days to D + 360 days,. However, the document does not mention staggered delivery (lot-wise) delivery requirements. Kindly confirm whether it is permissible to supply the entire quantity of solar modules at one go within the specified delivery window, or if staggered/lot-wise delivery is mandatory. | Contractual | Kindly refer clause 3 of SPC Section as quoted below: Under the above-mentioned total timelines of 12 months, PV Modules including Mandatory Spares under the award shall be supplied by the supplier in staggered deliveries during the delivery window of 8 months from (D+120 to D+360) days.
17 | SECTION – VII | 235 | 2.1 | IS 14286: Part 1: 2019, Terrestrial Photovoltaic (PV) Modules - Design Qualification and Type Approval, Part 1: Test Requirements (Second Revision) | We want to state that DCR BIS certification and other reliability tests will be completed till June 2026 | Technical | Availability of all test reports and certifications as per tender shall be ensured at the time of detailed engineering.
18 | SECTION – VII | 244 | 8.4 | Insulation test: IS 14286: Part 2: 2019, 4000 V for 1 min and 1500 V for 2 min | As per PDI sample size, 4000V for 1 min and 1500V for 2 min cycle time will be time consuming process considering the limited supply time provided in this tender. Request to kindly consider below revision towards the Insulation Tests Test Voltage: 4800V ( As per IEC), Ramp up Time: 6 Sec @500 V/Sec, Dwel Time:1 Sec, <50μA. And Voltage: 1500V (Module system voltage), Ramp up Time: 6 Sec @500V/Sec, Dwell Time:1 Sec, >40 Mohm.m2 | Technical | Terms and Conditions of the Tender shall prevail
19 | SECTION – VII | 244 | 8.4 | Continuity test of equipotential bonding: IS/IEC 61730-2: 2016, 2.5 times of the maximum overcurrent protection rating for 2 min | As per PDI sample size, 2 mins cycle time will be time consuming process considering the limited supply time provided in this tender. Request to kindly consider following revision: Applied Current: (Fuse Rating X 2.5 Amps), Time: 6 Sec, <0.01ohm | Technical | Terms and Conditions of the Tender shall prevail
20 | SFF | 171 | Para 3 & 4 | We further understand that the List-I (Solar PV Modules) of ALMM Order, Annexure-I of the OM, issued by MNRE on 10th March, 2021 will be updated by MNRE from time to time. We also understand that the Modules to be procured for this project, shall be from the List-I of the ALMM Order applicable on the date of invoicing of such modules. We further accept that Modules shall be manufactured using the Solar Cells enlisted in the ALMM – List II, as notified by MNRE Order No. 283/59/2024-GRID SOLAR. | As the tender document mention that "Module shall be from the List-I of the ALMM Order applicable on the date of invoicing of such modules." we understand that the cell used for the module also has to be listed in the ALMM-II list applicable on the date of invoicing of such modules. Kindly confirm on the same. | Contractual | Solar Modules and Solar Cells (used in BoM of the Module) shall be ensured to be included in the ALMM lists (List I and List II) at the time of Invoicing
21 | QUALIFYING REQUIREMENTS (QR) | 92 | 1.3 | The Minimum Average Annual Turnover (MAAT) of the bidder in the last three financial years (i.e. FY 2022-23, 2023-24 & 2024-25) should be INR 198.23 Crores/- (Indian Rupees One Hundred and Ninety-Eight Crores Twenty-Three Lakhs only). MAAT shall mean Revenue from Operations as incorporated in the profit & loss account excluding other income, e.g. sale of fixed assets. A summarized sheet of average turnover, certified by a practicing Chartered Accountant/Statutory Auditor should be compulsorily enclosed along with corresponding annual accounts. | Request to kindly change the criteria for MAAT for last 3 Financial Years from INR 198.23 Crores/- to INR 100 Crores /- | Contractual | The terms and conditions of the tender document shall prevail.
22 | QUALIFYING REQUIREMENTS (QR) | 92 | 1.3 | The bidder should have a minimum Working Capital of INR 165.19 Crores (Indian Rupees One Hundred and Sixty-Five Crores Nineteen Lakhs only) as per the last audited financial statement. If the bidder’s working capital is inadequate, the bidder should supplement this with a letter from the bidder’s bank, having net worth not less than INR 500 Crores, confirming availability of the line of credit for more than or equal INR 165.19 Crores (Indian Rupees One Hundred and Sixty-Five Crores Nineteen Lakhs only) to meet the working Capital requirement of this particular Project. | Bidder requests that the Financial Qualification Criteria to be relaxed and consider either MMAT or Working Capital as qualification requirement. Alternatively kindly keep the Min. Working Capital Requirement to be less than INR 50 Crores/- for last Financial Year. | Contractual | The terms and conditions of the tender document shall prevail.
23 | Technical Requirements | 235 | 3 | Dimensions -> Width: 1134 mm +/- 2 mm | Request you to kindly include the width 1303 +/- 2 mm as well. This will allow us to offer the higher wattage module (700+ Wp) with latest technology of G12 providing considerable saving in BoS cost ~5 lakhs/MWp. | Technical | Terms and Conditions of the Tender shall prevail
24 | Section V Special Purchase Conditions (SPC) | Page 3 of 10 | 6 | The value of the Contract Performance Security shall be 10% (Ten) of the Contract Value | We request to consider contract performance security to be 3% (three) of the contract value | Contractual | The terms and conditions of the tender document shall prevail.
25 | Section V Special Purchase Conditions (SPC) | Page 8 of 10 | 13 | Payment shall be released within 30 days of submission and acceptance of invoice by the Engineer In Charge, having following payment milestones as mentioned below. | We request as below: Payment shall be released within 15 days of submission and acceptance of invoice by the Engineer In Charge, having following payment milestones as mentioned below. | Contractual | The terms and conditions of the tender document shall prevail.
26 | SECTION - III BID DATA SHEETS (BDS) | Page 3 of 11 | 6 | The bid validity period shall be 180 (One Hundred and Eighty Days) from the date of opening of Techno-Commercial Bid (Envelope-I). | We request to keep the bid validity of 60 days | Contractual | The terms and conditions of the tender document shall prevail.
27 | INVITATION FOR BIDS (IFB)/BID INFORMATION SHEET | 16 of 18(19/258) | K | ONLINE BID-SUBMISSION DEADLINE - 10.03.2026 up to 1400 HRS | EMMVEE Requests to Extend the Bid Submission dates by 3-WEEKS AND provide new date with 31.03.2026 | Contractual | The bid submission deadline (if any) will be notified through the ETS Portal and SECI's website.
28 | SPECIAL PURCHASE CONDITIONS (SPC) | 8 of 10 (149/258) | 13 | Schedule of Rates & Payments Terms of 10%, 80% & 10% | SECI to Confirm the LC will be for 100 % of the Contract Value/ Emmvee Request for 20% advance and balance 80% payment through Letter of Credit for 30 days prior to commencement of production. EMMVEE request you to establish an irrevocable Letter of Credit (L/C) in favour of the supplier through the Employer's Bank for payments. | Contractual | The terms and conditions of the tender document shall prevail.
29 | BID DATA SHEETS (BDS) | BDS 3 of 11 (80/258) | 6 | Bid Validity-The bid validity period shall be 180 (One Hundred and Eighty Days) from the date of opening of Techno Commercial Bid (Envelope-I). | EMMVEE request to keep BID VALIDITY period to 30-days from date of opening of Techno-commercial bid. | Contractual | The terms and conditions of the tender document shall prevail.
30 | INVITATION FOR BIDS | 15 of 18(18/258) | (I) | CONTRACT PERFORMANCE SECURITY: 10% of the Total Project/Order Cost for a total period of 27 months. | Tender document Terms - 5% of Total PO VALUE EMMVEE Request to reduce it to 5% instead of 10%. | Contractual | The terms and conditions of the tender document shall prevail.
31 | SPC | 3 of 10 (144/258) | 6 (25.1) | The value of the Contract Performance Security shall be 10% (Ten) of the Contract Value (i.e., total sum of the Supply & Service Contract). This Performance security will be valid for a total period of 27 Months (12 Months Project completion period + 12 months of Defect Liability Period + 03 Months additional) from the date of its issuance. | Tender document Terms - 10% of Total PO VALUE EMMVEE Request to reduce it to 5% of PO Value instead of 10%. | Contractual | The terms and conditions of the tender document shall prevail.
32 | Defect Liability Period (GPC clause 53.2) | SPC 7 of 10 (148/258) | 3.2.13 | 53.2.13 Latent Defect Liability: Notwithstanding, the defect liability period of 12 months above, the contract shall carry a latent defect liability of 5 years from date of delivery of material at site towards any defects in the modules supplied by the Supplier. | Please delete Latent Defect Liability clause, as latent Defect liability is NOT applicable as per prevailing industry norms. | Contractual | The terms and conditions of the tender document shall prevail.
33 | BID DATA SHEETS (BDS) | 3 of 11 (80/258) | 7 | ZERO DEVIATION & REJECTION CRITERIA (ITB 18.1 & 18.2) Clause No. 18.1, Zero deviation & Clause No. 18.2, Rejection Criteria should be read in conjunction to each other & both clauses points mentioned should complement each other. | Unavoidable Deviations should be Allowed. | Contractual | All such events will be dealth on case to case basis considering the merit of the case and accordingly appropriate decisions will be taken.
34 | DOMESTIC CONTENT REQUIREMENT | IFB 7 of 18 (10/258) | 4 | For the supplies to be done under this tender, both the Solar Cells and Modules must be made in India and Modules shall be from the Manufacturers listed in ALMM list, published & updated by MNRE from time to time | ALMM at the time of last supply | Contractual | Solar Modules and Solar Cells (used in BoM of the Module) shall be ensured to be included in the ALMM lists (List I and List II) at the time of Invoicing
35 | INVITATION FOR BIDS (IFB) | IFB 5 of 18 (08/258) | 2.10 | Power Rating at STC ≥ 585 Wp | Tender specifies module power rating ≥ 585 Wp. Kindly clarify whether bidders can offer higher wattage modules (e.g. 600 – 620 Wp TopCon). Also confirm whether mixed wattage supply within tolerance band is acceptable. | Technical | 1. Higher wattage modules are admissible 2. Mixed wattage supply is admissible. 1, 2 hold provided all other Technical Specifications are met, the wattages fall within the same module family and not more than 3 module wattages are proposed. Please refer to Amendment No. 3.
36 | Section VII Scope of Supply and Technical Specifications (PART – A: SCOPE OF SUPPLY) | Page 3 of 20 | 1.4 | The Bidder shall offer only one type of PV Module with same Dimensions as per the specifications provided herein. The PV Module dimensions shall not change from the Guaranteed Technical Particular Datasheet (Form: T-01) provided with the bid. | Monocrystalline with n type (Topcon) cells G-G modules | Technical | Any module conforming to Technical Specifications is acceptable
37 | Section VII Scope of Supply and Technical Specifications (PART – A: SCOPE OF SUPPLY) | Page 4 of 20 | 1.5 | The Supplier shall submit PAN file of the PV Modules to be supplied (certified by an ILAC member signatory accredited laboratory) within 60 days from the date of Award. | Will it be acceptable if one or two bins PAN files are from laboratory and based on those one or two bins laboratory PAN files, other bins PAN files are internally submitted by manufacturer? | Technical | All submitted PAN file of the PV Module shall be certified by an ILAC member signatory accredited laboratory
38 | Section VII Scope of Supply and Technical Specifications (PART – A: SCOPE OF SUPPLY) | Page 6 of 20 | 2.1 | IS 14286: Part 1: 2019 Terrestrial Photovoltaic (PV) Modules - Design Qualification and Type Approval, Part 1: Test Requirements (Second Revision) | IS 14286 (Part 1) – 2010-is available and IS14286(Part-1)-2023 under testing , Emmvee modules have qualified for IEC 61215: 2021 which is equivalent to IS 14286 , No CRS Scheme available in BIS Portal | Technical | Module of proposed rating shall be tested as per standard mentioned in the technical specifications. Higher revision of standards specified are acceptable.
39 | Section VII Scope of Supply and Technical Specifications (PART – A: SCOPE OF SUPPLY) | Page 6 of 20 | 2.1 | IS 14286: Part 1: Sec 1: 2019 Terrestrial Photovoltaic (PV) Modules - Design Qualification and Type Approval, Part 1: Test Requirements, Section 1: Special requirements for testing of crystalline silicon photovoltaic (PV) modules (Second Revision) Additional Test Report for TOPCon Modules: UV Preconditioning with 50 cycles Thermal Cycles and 10 cycles Humidity Freeze Cycles as per IS 14286/IEC 61215 three times | IS 14286 (Part 1/Sec1) – 2019-is equivalent IEC 61215(Part 1/Sec 1)-2021. Our modules are qualified for IEC61215-2021. No CRS Scheme available in BIS Portal , Emmvee will provide 3xIEC report | Technical | Module of proposed rating shall be tested as per standard mentioned in the technical specifications. Higher revision of standards specified are acceptable.
40 | Section VII Scope of Supply and Technical Specifications (PART – B: TECHNICAL SPECIFICATIONS) | Page 6 of 20 | 2.1 | IS/IEC 61701: 2011: Salt Mist Corrosion Testing of Photovoltaic (PV) Modules – Severity 1 | Kindly confirm if manufacturer has- Severity - 6 test certificate as per IEC 61701: 2020. will it be acceptable? | Technical | Acceptable
41 | Section VII Scope of Supply and Technical Specifications (PART – B: TECHNICAL SPECIFICATIONS) | Page 6 of 20 | 3 | Module Efficiency - ≥ 21.65% & Power Rating at STC - ≥ 585 Wp | Please allow ≥ 580Wp modules | Technical | Terms and Conditions of the Tender shall prevail
42 | Section VII Scope of Supply and Technical Specifications (PART – B: TECHNICAL SPECIFICATIONS) | Page 8 of 20 | 5.2 | The modules shall be warranted for minimum of 10 years against all material/ manufacturing defects and workmanship. | Please consider : The modules shall be warranted for minimum of 10 years against all the defect which is impacting the performance of the modules. Excluding the defects which does not effecting the performance of modules. | Technical | Terms and Conditions of the Tender shall prevail
43 | Section VII Scope of Supply and Technical Specifications (PART – B: TECHNICAL SPECIFICATIONS) | Page 10 of 20 | 7.3 | For crystalline-Si modules current binning of modules shall be employed so that Maximum Power current (Imp) mismatch of modules in a bin does not exceed 200 mA | Please consider : Ist and 3rd bin Open | Technical | Terms and Conditions of the Tender shall prevail
44 | Section VII Scope of Supply and Technical Specifications (PART – B: TECHNICAL SPECIFICATIONS) | Page 11 of 20 | 7.5 | The Owner shall perform material inspection at the Manufacturer’s factory before the start of proposed manufacturing schedule. Proof of procurement of components as per the approved BOM mentioning manufacturer name, manufacturing date and relevant test certificate shall be submitted during material inspection for verification. | Please consider: The Owner shall perform material inspection at the Manufacturer’s factory either during modules manufacturing or during pre-dispatch Inspection. Proof of procurement of components as per the approved BOM mentioning manufacturer name, manufacturing date and relevant test certificate shall be submitted during material inspection for verification. | Technical | Terms and Conditions of the Tender shall prevail
45 | Section VII Scope of Supply and Technical Specifications (PART – B: TECHNICAL SPECIFICATIONS) | Page 10 of 20 | 7.1 | The cells used for module making shall be free from all defects like edge chipping, breakages, printing defects, discoloration of top surface etc. Only Class A solar cell shall be used. | Please consider: The cells used for module making shall be qualified as per manufacturer's quality acceptance criteria of Class A solar cell. | Technical | The material acceptance/rejection criteria shall be approved by the Employer as per the PV Module QAP submitted by the Supplier to SECI, prior to manufacturing.
46 | 4.0 Inspection Schedule | Page 12 of 20 | 4 | The Supplier shall propose the schedule for Pre-dispatch Inspection of finished goods to the Owner well in advance, and in no case less than 07 (Seven) days prior to commencement of inspection. Production Flash Test Results of the offered PV Modules shall be submitted to the Owner along with the inspection call. | 02 (TWO) days prior to commencement of inspection. & Pre Dispatch Inspection will be 5MW/lot | Technical | Terms and Conditions of the Tender shall prevail
47 | INVITATION FOR BIDS (IFB)/BID INFORMATION SHEET | 16 of 18(19/258) | K | ONLINE BID-SUBMISSION DEADLINE - 10.03.2026 up to 1400 HRS | EMMVEE Requests to Extend the Bid Submission dates by 3-WEEKS AND provide new date with 31.03.2026 | Contractual | The bid submission deadline (if any) will be notified through the ETS Portal and SECI's website.
48 | SECTION - VII: Scope of Work & Technical Specifications | 230 | 1.1 | PV Modules shall be registered with Bureau of India Standards (BIS) and bear the Standard Mark as per Solar Photovoltaics, Systems, Devices and Components Goods (Requirements for Compulsory Registration) Order, 2017 and subsequent amendments. | We are having following versions for certification: IS 14286 (PART 1/SEC 1) : 2023/ IEC 61215-1-1: 2021 & IS/IEC 61730-1: 2016 & IS/IEC 61730-2: 2016 | Technical | Higher revision of standards specified are acceptable. Terms and Conditions of the Tender shall prevail
49 | SECTION - VII: Scope of Work & Technical Specifications | 235 | 5.4 | The use of robotic cleaning systems shall not invalidate or limit the applicability of the recommended cleaning practices. | An accelerated lifecycle test of the proposed robotic cleaning system on Premier Solar modules shall be conducted at a third-party accredited laboratory. Based on the third-party test report, a compatibility declaration will be issued for the specific make and model of the robotic cleaning system. Any Pmax degradation observed during the accelerated lifecycle testing of the robotic cleaning system shall be amortized and included in the annual performance degradation as declared in the module warranty certificate. | Technical | Terms and Conditions of the Tender shall prevail
50 | SECTION - VII: Scope of Work & Technical Specifications | 235 | 5.4 | Any damages to the PV Modules, including but not limited to scratches, coating degradation, delamination, frame distortion, or water ingress, arising due to incompatibility with robotic cleaning systems operated within the specified conditions of suppliers recommended cleaning practices,, shall be deemed a manufacturing defect and shall be covered under the Product Warranty. | The Product Warranty shall not apply to any cosmetic or appearance-related deterioration that occurs naturally after shipment from PEL, including but not limited to scratches, stains, mechanical wear, rust, mold, surface degradation, discoloration, or other visual alterations, provided such conditions do not impact the power output, performance, or mechanical integrity of the PV modules. Further, cell finger discoloration, cell busbar discoloration, and/or snail trails shall be considered non-warranty items and shall not be covered under the Product Warranty. | Technical | The defects listed in the query — including snail trails, discoloration, scratches, mechanical wear, and rust — are indicative of issues that may impact the reliability of the modules in the field. Accordingly, Product Warranty shall apply to these defects. The burden of demonstrating that any such defect is without impact on performance, mechanical integrity, or long-term reliability shall rest with the supplier
51 | SECTION - VII: Scope of Work & Technical Specifications | 253 | 3 | Corrosion Protection Category:C4 | The offered PV modules are tested and compliant with IEC 61701:2011, having successfully passed Severity Level-6 (Salt Mist Corrosion Test). Kindly confirm whether this compliance is acceptable as meeting the C4 corrosion protection category requirement specified in the tender. | Technical | Acceptable
52 | SECTION - VII: Scope of Work & Technical Specifications | 253 | 3 | Holes positions and Design Load requirements: 400 mm- 1400 ps 790 mm-1700Pa 1400 mm- 2000Pa | The offered PV modules have the following hole positions and corresponding design load ratings: 400 mm – 1065 Pa 790 mm – 1200 Pa 1400 mm – 1600 Pa load on back & 2000Pa load on front Kindly confirm whether the above hole positions and design load capacities are acceptable in lieu of the tender-specified requirements. | Technical | Terms and Conditions of the Tender shall prevail
53 | General Purchase Conditions | 13 of 43 | 20 | Force Majeure | Suitable language to be inserted clarifying that payment obligations under the Agreement shall not be suspended due to any force majeure event. | Contractual | All such events will be dealth on case to case basis considering the merit of the case and accordingly appropriate decisions will be taken.
54 | General Purchase Conditions | 18 of 43 | 26.2.3 | The term "Abandon" has not been defined.. | To be defined. | Contractual | In general terms it means non-performance of the contractual obligation by the supplier. However, all such events will be dealth on case to case basis considering the merit of the case and accordingly appropriate decisions will be taken.
55 | General Purchase Conditions | 14 of 43 | 20.7 | Force Majeure If supply is suspended by Force Majeure conditions lasting for more than two months, the Owner shall have the option of cancelling this Contract in whole or part thereof, at its discretion. | However, upon such cancellation, the Supplier shall be entitled to payment for: (i) all supplies, goods, materials and equipment already delivered to the Site and accepted by the Owner; and (ii) all work‑in‑progress, including partially completed goods, components, and materials reasonably procured or manufactured for the purpose of the Contract, to the extent such work‑in‑progress is capable of being delivered to or used by the Owner. | Contractual | All such events will be dealth on case to case basis considering the merit of the case and accordingly appropriate decisions will be taken.
56 | General Purchase Conditions | 15 of 43 | 21.2 | The Owner shall at its sole discretion upon reaching the maximum LD limit , as an alternative to the Liquidated Damages at its option, get supply executed from elsewhere at the risk and cost of the Supplier irrespective of the fact whether the scope of Contract is identical to the original scope of Contract and in case the Owner chooses the alternative course as mentioned, it will be entitled to recover compensation/ damages from the Supplier irrespective of maximum limit prescribed under Clause 21.1. | Upon the Liquidated Damages reaching the maximum limit prescribed under Clause 21.1, the remaining supply shall first be offered to the Supplier to arrange completion through a third‑party agency at the Supplier’s own cost and risk. The Supplier shall, within a reasonable period notified by the Owner, propose a third‑party agency for completing the balance supply. Such third‑party shall be required to meet the technical and delivery requirements of the Contract. Only in the event that the Supplier fails to propose such a third‑party within the stipulated period, or the proposed third‑party does not meet the contractually defined technical and delivery requirements, may the Owner proceed to get the balance supply executed from any other source at the risk and cost of the Supplier. | Contractual | The terms and conditions of the tender document shall prevail.
57 | General Purchase Conditions | 15 of 43 | 21.3 | The Owner may by giving (01) one-month notice to the Supplier cancel the Contract without prejudice to the Owner’s right under Clauses 21.1 and 21.2 or any other provisions contained in the Contract to determine the Contract and claim damages from the Supplier. | Owner should not have right to terminate on convenience. Else the below need to be incorporated. Provided, however, that in the event of such cancellation under this clause, the Owner shall pay the Supplier: (i) all costs reasonably and properly incurred by the Supplier up to the effective date of cancellation, including the cost of all supplies, work‑in‑progress, materials, components, sub‑supplier commitments, and demobilization; and (ii) an additional amount equivalent to thirty percent (30%) of such costs, towards overheads, profit, loss of opportunity, and consequential impact of early termination. | Contractual | The terms and conditions of the tender document shall prevail.
58 | General Purchase Conditions | 15 of 43 | 22 | Rights of the Owner to forfeit Contract Performance Security | To add: Provided, however, that such recovery from the Contract Performance Security or any other sums due to the Supplier shall be limited only to those claims which are (i) mutually agreed and accepted in writing by the Supplier, or (ii) determined as payable pursuant to the dispute resolution mechanism under the Contract. | Contractual | All such events will be dealth on case to case basis considering the merit of the case and accordingly appropriate decisions will be taken.
59 |  |  |  | General | Under no circumstances shall the Owner have the right to terminate the Contract unilaterally/at convenience unless there is a breach by the Supplier, and such breach has not been remedied by the Supplier within a reasonable cure period | Contractual | The terms and conditions of the tender document shall prevail.
60 | General Purchase Conditions | 17 of 43 | 26.1 | Termination for Owner’s Convenience | Either this clause be deleted or include below as part of compensation. (an additional amount equivalent to thirty percent (30%) of such costs, towards overheads, profit, loss of opportunity, and consequential impact of early termination.) | Contractual | The terms and conditions of the tender document shall prevail.
61 | General Purchase Conditions | 18 of 43 | 26.2.3 | Termination for Supplier’s Default | Cure period be 30 days at least. | Contractual | The terms and conditions of the tender document shall prevail.
62 | General Purchase Conditions | 20 of 43 | 27 | Members of the Owner not individually Liable | Should be made mutual. | Contractual | The terms and conditions of the tender document shall prevail.
63 | General Purchase Conditions | 21 of 43 | 31 | Sub-letting of supplies | Written consent be replaced with prior intimation to ensure no unnecessary delays. | Contractual | The terms and conditions of the tender document shall prevail.
64 | General Purchase Conditions | 24 of 43 | 35.2 | Delays by Owner or his Authorized representatives | Cost compensation to be provided by owner for delays caused by them. | Contractual | The terms and conditions of the tender document shall prevail.
65 | General Purchase Conditions | 26 of 43 | 42 | Change in Law | Exclusions be deleted. | Contractual | The terms and conditions of the tender document shall prevail.
66 | General Purchase Conditions | 30 of 43 | 51 | Suspension of Supply | Provided, however, that in the event of such cancellation under this clause, the Owner shall pay the Supplier: (i) all costs reasonably and properly incurred by the Supplier up to the effective date of cancellation, including the cost of all supplies, work‑in‑progress, materials, components, sub‑supplier commitments, and demobilization; and (ii) an additional amount equivalent to thirty percent (30%) of such costs, towards overheads, profit, loss of opportunity, and consequential impact of early termination. | Contractual | The terms and conditions of the tender document shall prevail.
67 | Scope of Supply & Technical Specifications | 6 of 20 | 3 | Dimensions: Width: 1134 mm +/- 2 mm | As per given details only width has been mentioned, please clarify if both M10R & G12R modules can be supplied | Technical | M10R & G12R modules are admissible for supply, provided other technical specifications mentioned in the tender are met. However, only one module type shall be permitted per supplier (as per Tender)
68 | Instructions to Bidders | 11 of 56 | 11 | Unless stated otherwise in the Tender Documents, the Contract shall be for the whole works as described in Tender Documents, based on the rates and prices submitted by the Bidder and accepted by the Owner. | As per the given details, our understanding is that the applicable GST rate for the entire contract value would be 5% of the total contract value. Please clarify | Contractual | The bidders must mandatorily quote the GST for Modules Supply and Module Freight part in line with the current prevailing GST rate as per the applicable HSN Code. The bidders are required to exercise utmost diligence in mentioning such GST % , else SECI reserves all rights to correct the taxation part so as to arrive at the right taxation percentage & thereby the final total cost (If corrected).
69 | Scope of Supply & Technical Specifications | 6 of 20 | 2 | Standards | SECI to confirm whether the certification w.r.t. standards mentioned in 2 is required to be provided at the time of bid submission or after award of contract. | Technical | Shall be submitted by the Successful Bidder during detailed engineering
70 | General Purchase Conditions | 26 of 43 | 42 | The term Change in Law shall refer to the occurrence of any of the following events pertaining to this supply only after the date seven (7) days prior to the date of Bid submission, including (i) the enactment of any new law; or (ii) an amendment, modification or repeal of an existing law; or (iii) any change in the rates of any Taxes including any duties and cess or introduction of any new tax made applicable for setting up the project | Change in Law clause covering change in duty structure for raw materials has not been covered. Kindly add. | Contractual | The terms and conditions of the tender document shall prevail.
71 | Section - I | 8 | 2.1 | Monocrystalline Si TopCON Cells, Glass-Glass Modules with Al Frames Module Efficiency ≥ 21.65% Power Rating at STC ≥ 585 Wp | Can bidding be offered for both M10R & G12R modules as well? | Technical | M10R & G12R modules are admissible for supply, provided other technical specifications mentioned in the tender are met. However, only one module type shall be permitted per supplier (as per Tender)
72 | Section – VII | 236 | 3 | Holes positions and Design Load requirements | Is design load requirement inclusive of safety factor or exclusive of safety factor? | Technical | These are design loads, excluding the safety factor. Safety factor shall at least be 1.5, as per IS 14286
73 | Section - I | IFB (Pg 7 of 18) | 4 | Domestic Content Requirements For Cells | 1) Currently our cell facility is not listed in ALMM List - II, however, it shall be approved before the supply of this project starts. Thus, we request you to consider our undertaking as per FORM F-9 with the details our cell manufacturing facility. 2) Also, kindly consider FORM T-01 in this regards only. | Technical | Acceptable
74 | Bid Information Sheet | IFB (Pg 15 of 18) | H | Earnest Money Deposit (EMD) | Kindly reduce the EMD Amount per package or please fixate the EMD Amount to 1 value for all lots/packages instead of multiplying it as per package (x2 or x3). | Contractual | The terms and conditions of the tender document shall prevail.
75 | Section V - Special Purchase Conditions (SPC) | SPC (Pg 8 of 10) | SPC No. 13 (GPC Clause 78) | Schedule of Rates & Payments | 1. Kindly reduce the % of ABG against Advance from 110% to 10% only. Otherwise, please allow for submission of Corporate Guarantee (CG) instead of ABG. 2. Kindly specify the mode of the payment - irrevocable L/C (Letter of Credit) or Cash Payment on pro-rata basis or quarterly basis. | Contractual | The terms and conditions of the tender document shall prevail.
76 | Section - II | ITB (Pg 24 of 56) | 31.4 | Evaluation Criteria | 1. Under Adjustments (due to BoS), kindly clarify how is the number (-4,51,126) fixated or taken. Is it permanent in nature or dependent on individual manufacturers? 2. As per the sign convention, the adjustment value is negative, then kindly clarify if this value is being removed/reduced from Quoted Bid Value (QBV) or not. 3. Kindly clarify whether the EBV will be considered for Price/MW (including GST) & will consequently decide from where the eRA will start or not. | Contractual | 1. The number of negative 4,51,126 is fix in nature and same for all the participating bidders and the number has been arrived on the basis of simulation exercise carried out by SECI. 2. As the increase in PV module efficiency results in a lower number of modules required to achieve the same installed capacity. This, in turn, leads to a reduction in Balance of System (BoS) cost, owing to decreased expenditure on trackers, DC cabling, module mounting structures (MMS), foundations, and other associated components. The “Adjustment due to BoS cost” has been derived based on the cost reduction in BoS components resulting from improved module efficiency. To incorporate this impact, the parameter is introduced in the Evaluated Bid Value (EBV) computation. On the basis of the Module Efficiency quoted by the bidder w.r.t. the reference efficiency, suitable Adjustment Value will be calculated by SECI and same will be used to arrive at the Evaluated Bid Value as per the formula specified in the Evaluation Criteria of the tender document. 3. Yes, the EBV as calculated from the formula will be in INR/MW inclusive of GST and the same will be used for the purpose of ranking of bidders and e Reverse Auction.
77 | Section V - Special Purchase Conditions (SPC) | SPC (Pg 2 of 10) | 3 | Definitions (GPC Clause 1) | 1. As per our understanding, the delivery will start after 120 days from issuance of Purchase Order and will go on for 360 days (12 months) for whichever package we opt for. Kindly clarify if the there is a misinterpretation or not. | Contractual | Yes, the delivery will be in staggered manner starting from (Zero Date + 120 days) till (Zero Date + 360 days). Zero Date will be date of signing of Purchase Order or Notice to Proceed (whichever is later).
78 | Section V - Special Purchase Conditions (SPC) | SPC (Pg 3 of 10) | 6 | Contract Performance Security (GPC Clause 25) | We request you to kindly consider CPBG for 3% for 12 months instead of 10% for 27 months and in terms of Insurance Surety Bond. | Contractual | The terms and conditions of the tender document shall prevail. However, submission of PBG in form of Surety Bond is allowed.
79 | ANNEXURE TO BID DATA SHEET | 90 | 1.1 | GENERAL ELIGIBILITY CONDITIONS: The Bid Processing Fees and EMD are exempted for eligible bidders who are registered MSEs under NSIC/ DIC/ Udyog Aadhaar Category only. As per Ministry of MSMEs (MoMSME) Gazette notification No. S.O. 4926(E) dated 18.10.2022 | We request you to include medium scale Entrepreneurs for exemption from Bid Processing Fees and EMD. Further we request for relaxation in Qualification Criteria for MSMEs. Kindly consider | Contractual | The Bid Processing Fees and EMD are exempted for eligible bidders who are registered MSEs under NSIC/ DIC/ Udyog Aadhaar Category only. As per Ministry of MSMEs (MoMSME) Gazette notification No. S.O. 4926(E) dated 18.10.2022 bidders will be eligible to avail all non-tax benefits of the category (micro or small or medium) it was in before the re-classification, for a period of three years from date of such upward change. In case the bidder proposes to meet the qualifying requirements based on the credentials of its Parent/Holding/Subsidiary/Affiliate and any its Parent/Holding/Subsidiary/Affiliate is not an MSE, the bidder will not be eligible for exemption of Bid Processing Fees and EMD.
80 | ANNEXURE TO BID DATA SHEET | 91 | 1.2 | TECHNICAL ELIGIBILITY CONDITIONS: The Solar PV Module manufacturer having a manufacturing facility capacity of minimum 435 MWp/ annum if: Submitting its bid for Package Capacity of 290 MWp | Whether a bidder participating for Single package have to produce a minimum manufacturing capacity of 435 MWp per annum cumulative for all types of modules (like HJT/TOPCON/Mono-PERC etc.), or a minimum 435 MWp per annum manufacturing capacity only for Topcon type of module is unclear/lacks clarity. Hence we request for clarification of this point and consider whole plant manufacturing capacity as one irrespective of Module Type. | Contractual | The Manufacturing Capacity of the plant irrespective of the type of Module Technology will be used for the purpose of Technical Qualification. However, bidder must ensure compliance with the ALMM List I and List II for the type of Module Specifications asked in the tender at the time of supply of such Modules.
81 | Capacity Configuration / Technical Requirements | IFB Page 5 of 18; SoS & TS Page 6 of 20 | Clause 2.10 | The Bidder must offer Monocrystalline Si TopCON Cells, Glass-Glass Modules with Al Frames, Module Efficiency ≥ 21.65%, Power Rating at STC ≥ 585 Wp. | We humbly request SECI to kindly allow Monocrystalline Si TopCON, Glass-Glass Modules with minimum power rating of ≥ 570 Wp while complying with minimum module efficiency ≥ 21.65% and all other technical and DCR requirements. | Technical | Terms and Conditions of the Tender shall prevail
82 | Section 1 | 5 | 2.1 | The Bidder must offer following Module Technology: Monocrystalline Si TopCON Cells, Glass-Glass Modules with Al Frames Module Efficiency ≥ 21.65% Power Rating at STC ≥ 585 Wp | We request Mono-PERC technology to be included as well. Power rating >= 585 Wp; efficiency >=21% | Technical | Terms and Conditions of the Tender shall prevail
83 | Section 7 | 6 | 3 | Temperature co-efficient of power: Not less than -0.30%/°C | Request the temperature co-efficient of power to be reduced to -0.35%/°C | Technical | Terms and Conditions of the Tender shall prevail
84 |  | 7 | 3 | Holes positions and Design Load requirements | Request the acceptance of mounting holes at 1000/1600 mm as well | Technical | Terms and Conditions of the Tender shall prevail
85 |  | 9 | 5.4 | Warranty for Compatibility with Robotic Cleaning Systems | Type of robot needs to be suggested, and based on the suggestion the technical and feasibility analysis can be performed. | Technical | Supply of the Robotic Cleaning System is in the Scope of the BoS Contractor. The successful bidder's module shall be tested with the Robotic Cleaning System proposed by the successful BoS Contractor.
86 |  | 10 | 5.5 | Warranty for Compatibility with Single Axis Tracker Systems | Request to consider fixed-tilt systems as well and not limit it to SAT. | Technical | Terms and Conditions of the Tender shall prevail
87 | Annexure to BDS | 3 | 1.2 | The Solar PV Module manufacturer having a manufacturing facility capacity of minimum 435 MWp/ annum if: Submitting its bid for Package Capacity of 290 MWp | Request to update the clause for bidder to have manufacturing capacity of both module & cell be 435 MWp/annum respectively. | Contractual | The terms and conditions of the tender document shall prevail. The Manufacturing Capacity as required in the Technical Eligibility Conditions of the QR section will only be verified from the List I of ALMM Order.
88 | ITB | 12 | 11.5 | Prices quoted by the Bidder, shall remain FIRM and Fixed and valid until completion of the Contract and will not be subject to variation on any account. | Considering the long delivery timeline of the project (12 months from NTP date), we request you to include a provision for price variation which will be dependent upon wafer & silver price. | Contractual | The terms and conditions of the tender document shall prevail.
89 | IFB | 16 | Bid Information Sheet K | Bid submission date is 10.03.2026 | As there are upcoming holidays in the next week due to Holi, we request the bid submission deadline to be extended by 2 weeks. | Contractual | The bid submission deadline (if any) will be notified through the ETS Portal and SECI's website.
90 | TS | TS | TS | General | In PART – B: TECHNICAL SPECIFICATIONS, point 3 outlines the technical requirements for hole positions and design loads. Specifically, it states a hole position (across the length of the module) of 790 mm. Our standard specification for this dimension is 990 mm. | Technical | Terms and Conditions of the Tender shall prevail
91 | BID INFORMATION SHEET | IFB Page 15 of 18 | CONTRACT PERFORMANCE SECURITY | 10% of the Total Project/Order Cost for a total period of 27 months | Requesting you to please wave off | Contractual | The terms and conditions of the tender document shall prevail.
92 | SoS & TS | Page 5 of 20 | PART B: TECHNICAL SPECIFICATIONS 1.3 | PV Modules to be supplied under this Contract shall be suitable for use with semiautomatic/ fully automatic robotic cleaning systems to be provided under the scope of the Owner / BoS Contractor selected by Owner. The Supplier shall certify that the modules (including glass, frame, and laminate, etc.) are robust against repetitive loads arising from robotic cleaning operations, and shall furnish supporting documents and/or third-party test reports demonstrating durability and compatibility for such cleaning systems prior to supply. | Please specify List of robotic cleaners approved | Technical | SECI does not maintain a list of approved makes of Robotic Module Cleaning Systems. The successful bidder's module shall be tested with the Robotic Cleaning System proposed by the successful BoS Contractor.
93 | SoS & TS | Page 5 of 20 | TECHNICAL SPECIFICATIONS 1.4 | configuration). Module supplier shall confirm that use of the modules on HSAT systems does not void performance warranty or product warranty obligations. | As per OEM Installation Manual | Technical | Terms and Conditions of the Tender shall prevail
94 | SoS & TS | Page 6 of 20 | 3 Technical Requirements | Dimensions Width:1134 mm +/- 2 mm | 2277 X 1133 (±2%) | Technical | Terms and Conditions of the Tender shall prevail
95 | SoS & TS |  | Rated power at STC | No negative tolerance is allowed | Pmax ±3% | Technical | Terms and Conditions of the Tender shall prevail
96 | SoS & TS |  | Temperature co-efficient of power | Not less than -0.30%/°C | 0.2915 % /°C | Technical | Terms and Conditions of the Tender shall prevail
97 | SoS & TS | Page 12 of 20 | 6 Sampling Process | Flash Test Special inspection level S-4 | General inspection (G1) | Technical | Terms and Conditions of the Tender shall prevail
98 | SoS & TS | Page 12 of 20 | 6 Sampling Process | Electroluminescence Special inspection level S-2 | General inspection (G1) | Technical | Terms and Conditions of the Tender shall prevail
99 | SoS & TS | Page 12 of 20 | 6 Sampling Process | Electrical Characteristics Special inspection level S-2 | General inspection (G1) | Technical | Terms and Conditions of the Tender shall prevail