## Compiled Pre Bid Queries
Balance of System tender for setting up of grid connected 200 MW Ground mounted Solar PV plant at Dhar, Madhya Pradesh
Tender No : SECI/C&P/OP/11/017/2024-25
S.No. | Tender Section | Page No. | Clause No | Description as per Tender Document | Queries | Category (Technical/Contractual) | Clarifications
1 | SECI000214-4632904-SA-ATentativeLandLayoutandContourDetails |  |  | Provided layout and contour details in pdf file | Bidder Requesting for KMZ file | Technical - Civil | KMZ file is not available. Refer to Sl. No. 56 of Amendment-1. CAD file has been shared.
2 |  |  |  |  | Bidder Requesting to provide SLD | Technical - Electrical | Plant SLD is in the scope of bidder, to be finalised during detailed engineering.
3 | SECI000214-1811828-TechnicalTenderDocument | 3 | 1.Project particulars | Supply of PV Modules at the Project Site shall be in the Scope of the Owner. The Owner shall deliver PV Modules at the Project site. However, for the purpose of bidding contractor may consider 540Wp Mono PERC module of 20.9% efficiency with dimensions 2278mm x 1134mm. | Bidder requesting to provide PAN file and datasheet of PV module and losses to consider | Technical - Electrical | PAN File of the final module shall be provided to the successful bidder. However for Bidding Purpose Bidder may consider 540Wp Mono PERC module. For Losses and other technical details, please refer to Sl. No. 16 of Amendment-1: SA - B: Project Specific Technical Details
4 | SECI000214-1811828-TechnicalTenderDocument |  |  |  | Bidder requests to provide Pitch and Tilt angle to consider | Technical - Electrical | Please refer to Sl. No. 16 of Amendment-1 : SA - B: Project Specific Technical Details
5 | SECI000214-1811828-TechnicalTenderDocument | 4 | 1.Project particulars | Cumulative Power Transformer Capacity-250 MVA (2 X 125 MVA) Plant End Substation Power Transformer (33/220 kV) Capacity-200 MVA (2 X 100 MVA) | Bidder requesting to confirm the power transformer capacity to consider. | Technical - Electrical | Power Transformer: 250MVA (125 x 2). Please refer to Sl. No. 17 Amendment-1
6 | SECI000214-1811828-TechnicalTenderDocument |  |  |  | Bidder requesting for shading time period to consider | Technical - Electrical | Query not clear.
7 | SECI000214-1811828-TechnicalTenderDocument | 4 | 3.1.2 | Soiling losses shall not be accounted for in the assessment of Results. Therefore, adequate Module cleaning exercise shall be undertaken prior to commencement of Commissioning process. | As per standard practice, for dry robotic cleaning , Soiling loss is considered. Bidder requesting to confirm on the same. | Technical - Electrical | Bidder shall select Manual / Semi-automatic / Robotic module cleaning system with either dry or wet cleaning method based on site conditions. However, the offered solution must ensure effective soiling removal, be compatible with the module mounting structure proposed by bidder, and meet O&M efficiency.
8 | SECI000214-1811828-TechnicalTenderDocument | 10 | 3.7.2 | Reactive power control The PCU shall be able to inject /absorb reactive power to/ from the grid based on the set point provided through PCU front control panel. The same shall be performed automatically with adjustable ramp rate based on dynamic changes in grid voltage or reactive power reference. | Bidder request to confirm whether to consider usage of SVG also for reactive power compensation. | Technical - Electrical | Yes. Bidder may consider SVG for reactive power compensation, as per the requirements for connectivity under GNA Regulations notified by CERC. Please refer clause No. 3.9 of SS-A: SOW.
9 | SECI000214-1811828-TechnicalTenderDocument | 4 | 1.Project particulars | Performance Ratio (at 220 kV side of Plant Pooling Substation)-81.1% | Bidder request to confirm the type and percentage of losses to consider | Technical - Electrical | Please refer to Sl. No. 16 of Amendment-1 : SA - B: Project Specific Technical Details
10 | SECI000214-1811828-TechnicalTenderDocument | 120 | 6.9 | Maintenance pathways of min. 1.0m width shall be provided between SPV arrays for easy movement of maintenance staff, tools, equipment and machinery, washing of modules etc. The pathway area shall be generally levelled and well compacted manually/ mechanically. Areas of depression, valley zones or wherever there is noticeable change in topography, shall be levelled using well compacted good granular earth matching the top finished surface with ground topography/ grade to avoid accumulation of water in the region and allowing its free flow to keep the area devoid of mud/ sludge. | Bidder is requesting to confirm Maintenance Pathways of min. 1.0m width shall be levelled manually/mechanically of the existing ground surface. | Technical - Civil | Query not clear; The terms and conditions of the tender document shall prevail.
11 | SECI000214-1811828-TechnicalTenderDocument | 118 | 5.3 | It is envisaged that the MMS are installed on natural/ existing ground without any levelling or grading of the area. Contractor shall accordingly consider the effect of the existing ground slope on the design of MMS structure as specified elsewhere in the specifications. If any ground undulations at column locations are observed the same shall be filled up with PCC (1:3:6) up to surrounding ground level immediately after pile installation before start of erection of other MMS members. In case of pile, the PCC fill shall extend min. 500mm outside pile cap all around and remaining area may be filled up with local soil properly compacted. | Bidder is requesting to confirm that PCC(1:3:6) shall extend min. 500mm outside pile cap incase of any ground undulations, and the remaining area of PV area shall be filled with local soil property (or) the existing ground should be compacted. | Technical - Civil | The requirement is applicable for the areas of local depressions where MMS column locations are falling. Further, refer to Sl. No. 1 of Amendment-1.
12 | SECI000214-1811828-TechnicalTenderDocument | 124, 125 | 10.10.1 | Module Mounting Structure (MMS) (additional requirements): The bidder shall conduct wind tunnel studies for the design and analysis of complete MMS, and the following shall be ensured: 1. It must be done from an institute of repute having suitable wind tunnel facilities (IITs, SERC Chennai or equivalent level institute in India.) 2. If the studies done by any reputed international facility, the study results must be vetted by the wind domain expert at any of the IITs or SERC or equivalent level institute in India. 3. Wind tunnel studies shall be specific to the site topography as well as array layout and shall be conducted in BLT tunnel as per guidelines specified in IS:875 – part 3 and ASCE MOP 67. 4. The wind tunnel studies shall be conducted with appropriate scale (however, not less than 1:50) model in boundary layer tunnel. | Bidder request to confirm whether the additional requirements of MMS-wind tunnel studies should be considered for the design and analysis of complete MMS and also request to confirm whether theses tests are considered to be mandatory. | Technical - Civil | The requirement of wind tunnel studies is mandatory for estimation of wind loads on the PV Modules. The member wind loads shall be calculated as per IS 875 Part 3. Further, refer to Sl. No. 2 of Amendment-1.
13 | SECI000214-1811828-TechnicalTenderDocument | 127 | 12.2.1 | In case the contractor proposes to provide bored cast-in-situ concrete pile; the type, dia. and length of pile shall be as per recommendations of Geotechnical investigation report corresponding to prevalent soil characteristics at site. However, the min. dia and depth of the pile shall be 300mm (Min 350 mm for column depth more than 175 mm) and 1500 mm respectively except when very hard strata/ rock (N>100) is encountered at a higher level, the pile shall be extended in to the hard strata minimum 1.5 times the diameter of the pile with total depth of the pile not less than 1200mm below cut-off level. A minimum clear cover of 50 mm shall be provided to the steel section or reinforcement in the pile. | Bidder request to confirm, if the column depth is more than 175mm whether we should have to follow 300mm or 350mm and if the hard strata/rock is encountered, whether we should have to consider the min 1.5times the diameter of the pile or it should not be less than 120mm below cut-off level or it should be followed according to the design requirements based on the SBC values. | Technical - Civil | Refer to Sl. No. 4 of Amendment-1.
14 | SECI000214-1811828-TechnicalTenderDocument | 127 | 12.2.2 | As specified above, the MMS support shall project minimum 200mm above FGL (Finished grade level) to avoid any damage to the MMS column/sub support due to direct contact of rain water/ surface run-off. This shall be ensured through either single stage construction of entire pile length including portion above FGL or by two stage construction. | Bidder request to confirm whether the MMS support is nothing but the pile cap which we have to project minimum 200mm above FGL. | Technical - Civil | The terms and conditions of the tender document shall prevail.
15 | SECI000214-1811828-TechnicalTenderDocument | 125 | 10.10.2 | WL shall be considered as detailed below for estimation of WL on members of MMS | Bidder request to confirm whether the type of loading for the same whether it should be UDL/Eccentric loading and as per the IS:875 Part-3 loading should be considered as Eccentric loading, please confirm. | Technical - Civil | Refer to Sl. No. 3 of Amendment-1.
16 | SECI000214-1811828-TechnicalTenderDocument | 131 | 13.7 | Module Mounting Structure (MMS) - Material specifications & coating for structural steel works Coating reference code-90 microns minimum (IS 4759/ IS 4736/ IS 2629) | Bidder request to confirm whether Coating reference shall be followed as HDG-90 Microns or otherwise bidder can also opt for other structure materials like Magsure/Magnelis. | Technical - Civil | Refer to Sl. No. 5 of Amendment-1.
17 | SECI000214-1811828-TechnicalTenderDocument | 133 | 13.11 | The purlins shall be provided with min. following tie/sag rods or angles or channels: • 1 no., in the mid of each span and shall connect all the purlin members • 1 no., diagonal, at each corner in end spans | Bidder request to confirm tie/sag rods should have to be considered 1 no in the middle of each span of the table and 1 no diagonal at each corner in end spans | Technical - Civil | The terms and conditions of the tender document shall prevail.
18 | SECI000214-1811828-TechnicalTenderDocument | 133 | 13.14 |  | Diagonal bracings will be considered and followed as per the design requirements. Please confirm | Technical - Civil | Refer to Sl. No. 6 of Amendment-1.
19 | SECI000214-1811828-TechnicalTenderDocument | 134 | 13.23 | 13.23 Fasteners and washers to be used for erection of mounting structure and for fixing the module shall be of stainless steel grade SS 304, with property class A2-70 conforming to relevant ISO standard and must sustain the adverse climatic conditions to ensure the life of the structure for 25 years. | Bidder request to confirm all the MMS structure connections should be considered as stainless steel grade SS304 only or otherwise bidder can also opt for Module-Purlin connections-SS304 & all other MMS structure connections as HDG | Technical - Civil | Refer to Sl. No. 7 of Amendment-1.
20 | SECI000214-1811828-TechnicalTenderDocument | 133 | 13.9 | • Vertical deflection for Rafter and Purlin – Span/ 180 • Lateral deflection for Purlin – Span/240 | Bidder request to confirm, if rafter is considered as a cantilever span can we consider Span/150, same for Purlin overhang. | Technical - Civil | The terms and conditions of the tender document shall prevail.
21 | SECI000214-1811828-TechnicalTenderDocument | 134 | 13.27, 13.28 | MMS column post supported with base plate secured to foundation shall be fixed with galvanized high strength “J” bolts conforming to specifications of IS: 4000/ IS: 1367 and relevant IS code. Installation of foundation bolts and embedment of column leg in foundation concrete shall be done by using template to ensure proper alignment. The underside of base plate shall be provided with anti- shrink grout. In case the contractor proposes to extend the column leg to embed it in the pile/pedestal as an alternate fixing arrangement, the column member shall be extended for full depth of the pile (100mm cover at tip of the pile) with an end plate of min. 4mm thickness, projecting min. 50 mm beyond the face, to be welded at the bottom of column leg or an angle section of minimum 2mm thick to be bolted on either face of the column web at bottom end of the column (However, for plants in coastal area or in case of marshy soil ) the column post shall be supported only with base secured to foundation through base plate and anchor bolt assembly as per Cl. No. 13.27 and no embedment of column leg in foundation is permitted). | Bidder request to confirm whether the end plates for column leg are mandatorily need to be considered. | Technical - Civil | The terms and conditions of the tender document shall prevail.
22 | SECI000214-1811828-TechnicalTenderDocument | 135 | 13.36 |  | Bidder request to confirm whether the mentioned no of bolts are mandatory or can be reduced as per design requirements. | Technical - Civil | The terms and conditions of the tender document shall prevail.
23 | SECI000214-1811828-TechnicalTenderDocument | 135 | 13.33 | The length of any cold formed section (CFS) generally shall not be more than 5.5 m. | Bidder request to confirm whether the following Point was applicable to the Purlin and should be considered accordingly. | Technical - Civil | The terms and conditions of the tender document shall prevail.
24 | SECI000214-1811828-TechnicalTenderDocument | 150 | 35.1, 35.2 | PV Module Cleaning System-Wet Cleaning/Dry Cleaning | Bidder request to confirm whether we should have to consider the Wet Cleaning System/Dry Cleaning System. If robotic cleaning system need to be considered, in that case the structure material for MMS Docking & Reverse Station should also need to be considered in the MMS weight. Please confirm | Technical - Electrical | Bidder shall select Manual / Semi-automatic / Robotic module cleaning system with either dry or wet cleaning method based on site conditions. However, the offered solution must ensure effective soiling removal, be compatible with the module mounting structure proposed by bidder, and meet O&M efficiency.
25 | SECI000214-1811828-TechnicalTenderDocument | 124 | 10.6 | Topography factor ‘k3’ shall be taken as 1.0 upto upwards slope of 3°. For topography with upward slope greater than 3°, the value of ‘k3’ shall be calculated as per Annexure-C of IS 875 (Part-3). | Bidder request to confirm whether this Topography factor need to be considered during design and analysis in STAAD Pro Software. | Technical - Civil | The terms and conditions of the tender document shall prevail.
26 | VII | 114,116,122,131,132/316 |  | Error! Reference source not found | A hyperlink error has been found on the pages mentioned. Kindly provide the appropriate contract clause for reference. | Technical - Civil | Refer Sl No. 8 to 12 of Amendment 1.
27 | VII | 133/316 | 13.14 | The vertical diagonal bracing shall be provided in end spans and every alternate span for all rows of columns of each unit (table) of MMS | As per IS 800:2007, cl 3.10.3.1, bracing may kindly be allowed at both end spans and the centre span instead of alternate spans | Technical - Civil | Refer to Sl. No. 6 of Amendment-1.
28 | VII | 133/316 | 13.22 | Two numbers of anti-theft fasteners of stainless steel on two diagonally opposite corners for each module shall be provided | In case a clamp system is used, the requirement may kindly be waived. Kindly confirm | Technical - Civil | The terms and conditions of the tender document shall prevail.
29 | VII | 142/316 | 17.4 | Battery Area/Room: Acid/ Alkali resistant tile flooring and 2100 mm height dado, | In case a dry battery is used, the requirement may kindly be waived. Kindly confirm. | Technical - Civil | The terms and conditions of the tender document shall prevail.
30 | VII | 149/316 | 34.2 & 34.3 | In case of transformer oil tank capacity ≥ 2000 litres, the transformer foundation shall have its own soak pit ……….& In case of transformer oil tank capacity more ≥ 5000 litres, the soak pit shall be connected to a separate burnt oil pit through GI discharge pipe ( | Kindly allow compliance with the Central Electricity Authority (Measures Relating to Safety and Electric Supply) Regulations, 2023 instead of the outdated provisions mentioned in the tender. | Technical - Civil | Refer to Sl. No. 57 & 31 of Amendment-1.
31 | VII | 11/316 | 4.1 | Module supply : between 6 (six) to 11 (eleven) months from date of award of the Contract. | In case of delays in module supply or any change in make/model during the 12-month commissioning period, a suitable time extension must be granted to allow for re-design and execution. | Contractual | All such cases will be dealt on case to case basis. However, incase of delay in Module supply from SECI's end suitable extension time will be provided.
32 | VII | 12/316 | 4.13 | 33 kV Over Head Transmission Line / Under Ground Cable including Poles / Towers, Conductors, Insulators, Cable Termination Kits and associated accessories from 33 kV Switchgear of inverter stations to 33/220 kV Pooling Substation including Right of Way, permits and approvals. | Kindly remove the 17 km of transmission line ROW responsibility from the bidder’s scope. | Contractual | The terms and conditions of the tender document shall prevail.
33 |  |  | General |  | Kindly provide the KMZ file and geotechnical investigation report for reference, if available. | Technical - Civil | KMZ file and geotech report are not available. Refer to Sl. No. 56 of Amendment-1. CAD file has been shared.
34 |  |  | General |  | It is understood from the topographical survey that a stream passes through the north and south blocks. Please confirm whether the stream is perennial. Additionally, can the vendor draw water from the stream for module washing? | Technical - Electrical | Water required for module cleaning has to be arranged by contractor only. Contractor can NOT draw water from the stream and must NOT disturb local drinking/agriculture water supply for module cleaning.
35 |  |  | General |  | The solar module GTP should be provided, including dimensions, pitch, and weight, to facilitate MMS design. The PAN file should also be furnished for PVsyst simulation. | Technical - Electrical | PAN File of the final module shall be provided to the successful bidder. However for Bidding Purpose Bidder may consider 540Wp Mono PERC module. For Module Dimensions and other technical details, please refer to Sl. No. 16 Amendment-1 SA - B: Project Specific Technical Details
36 | VII | 239/316 | Soiling loss | • Soiling losses shall not be accounted for in the assessment of Results. Therefore, adequate Module cleaning exercise shall be undertaken prior to commencement of Commissioning process. | Maintain 0% Soiling loss is not possible so please consider minimum 1.5% soiling loss during OTGT. | Technical - Electrical | The terms and conditions of the tender document shall prevail.
37 | VII | 7/316 |  | For Operational Acceptance-PR-81.1% | Please decide the PR during OTGT Test because Module parameter is not confirmed. | Technical - Electrical | For Operational Acceptance: OTF >= 1 (Kindly refer to GA-J: Functional Guarantee Test (OTGT) Procedure) Please refer to Sl. No. 24 & 25 of Amendment-1.
38 | VII | 309/316 |  | Liquidated Damages for Shortfall in Annual PR for Solar PV Plant | As per standard industrial practice for BOS solar tender , LD on PR or shortfall on generation shall be applicable from end of first year O&M -Please confirm the same. | Technical - Electrical | Liquidated Damages clause for Operational Acceptance and During O&M period has been updated. Please refer to Sl. No. 22, 24 & 25 of Amendment-1.
39 | ANNEXURE TO BDS | 6 of 11 | 1.3 | The bidder should have a minimum Working Capital of INR 94,00,00,000/- (Indian Rupees Ninety-Four crores only) as per the last audited financial statement. If the bidder’s working capital is inadequate, the bidder should supplement this with a letter from the bidder’s bank, having net worth not less than INR 500 Crores, confirming availability of the line of credit for more than or equal to INR 94,00,00,000/- (Indian Rupees Ninety-Four crores only) to meet the working Capital requirement of this particular Project. | 1. Please confirm whether the “last audited financial statement” referred to in the clause pertains to the Financial Year 2023–24. 2. In case the bidder’s working capital is inadequate, kindly clarify whether submission of a Line of Credit letter from the bank is mandatory, or if a general Bank Credit Letter will also be acceptable. | Contractual | For meeting the working capital requirement last audited financial statement i.e., FY 2023-24 will be consider. In case of inadequate working capital suitable line of credit must be submitted for the purpose of meeting the working capital requirement in line with the terms and conditions of the tender document.
40 | General |  |  |  | Can the Earnest Money Deposit (EMD) be submitted in the name of any one member of a Joint Venture (JV) or Consortium? | Contractual | In case of participation by a JV/Consortium, both EMD & PBG has to be mandatorily submitted in the name of JV/Consortium mentioning the names of all of the JV/Consortium members.
41 | General |  |  |  | Kindly share the KMZ With PSS location | Technical - Electrical | CAD file with tentative land boundary has been shared. Please refer Sl No. 56 of Amendment-1. The co-ordinate for Interconnecting S/S is provided at Sl. No. 26 of Amendment-1.
42 | General |  |  |  | What will be the Pole distance between two adjacent street lights? | Technical - Electrical | Average LUX level to be maintained in Internal / Access Roads shall be : 4 lux. Refer to Clause No. 20.3 and Clause no. 20.4.2 for more details.
43 | General |  |  |  | Kindly specify the NoS UG Water tank required. | Technical - Civil | Nos. of underground water tanks shall be as per system requirement to be finalized during detailed engineering.
44 | Sub section C Section VII | 44 of 58 | 35 | Module Cleaning System | Kindly confirm the technology of MCS. Manual/Robotic /semiautomatic Also, dry cleaning/wet cleaning? | Technical - Electrical | Bidder shall select Manual / Semi-automatic / Robotic module cleaning system with either dry or wet cleaning method based on site conditions. However, the offered solution must ensure effective soiling removal, be compatible with the module mounting structure proposed by bidder, and meet O&M efficiency.
45 | Sub section C Section VII | 13 of 58 | 6.2 | Roads Approach road - 4.0m+0.5m shoulder each Access road - 3.0m+0.5m shoulder each | What will be the width & Material of peripheral road? Please clarify | Technical - Civil | Refer Cl 6.10 (Page 14 of 58) of TS.
46 | Sub section C Section VII | 15 of 58 | 7 | Surface area drainage Storm water drainage | what will be the type of drain required in periphery. We will recommend earthen drain for the optimization of cost and fast construction. For storm water drain kindly clarify will it be RCC or stone lining? | Technical - Civil | The terms and conditions of the tender document shall prevail.
47 | Sub section C Section VII | 16 of 58 | 8 | Peripheral fence & main gate | which boundary have to consider for periphery either it is sola boundary or plot boundary. Also as KMZ is not available if there will be two three plots what will the number of gate required. | Technical - Civil | For peripheral fence, plot boundary needs to be considered with additional fence length wherever RoW needs to be provided. Refer Sl No. 56 of Amendment-1. Min. 1 No. of Main Gate shall be provided for an area under one common fence. In cae, the land parcels are non-contiguous or geographically separated, at least one Main Gate shall be provided in each distinct parcel of land, irrespective of its size.
48 | Sub section C Section VII | 33 of 58 | 16.2.3 | Storage cabin for plant spare | What will be the Size of PEB storage? | Technical - Civil | Size of storage cabin shall be finalized during detailed engineering as per the functional requirement.
49 | Sub section C Section VII | 34 of 58 | 16.2.4 & 16.2.5 | Security room & Watch tower. | NoS of Security room & Watch tower required? Kindly specify | Technical - Civil | The terms and conditions of the tender document shall prevail.
50 | Sub-Section A: SOW | 3 of 21 | 1 | Supply of PV Modules at the Project Site shall be in the Scope of the Owner. The Owner shall deliver PV Modules at the Project site. However, for the purpose of bidding contractor may consider 540Wp Mono PERC module of 20.9% efficiency with dimensions 2278mm x 1134mm. | Please Provide the Data Sheet Of The Module, please confirm the Module cable length it will be 1200 mm or 300 mm Also Please provide the Pan File For Generational Analysis, | Technical - Electrical | The Module cable length it will be 1200 mm. Please refer to Sl. No. 16 of Amendment-1 for SA-B: Site Specific Technical Parameters.
51 | Sub-Section A: SOW | 3 of 21 | 1 | Supply of PV Modules | Bidder request to considered Higher Wp Rating Module With Top Con Technology. | Technical - Electrical | For the purpose of bidding contractor may consider 540Wp Mono PERC module of 20.9% efficiency with dimensions 2278mm x 1134mm. However, actual modules supplied by Owner may be same or different (any of the Mono PERC, TopCon, Thin Film, etc.)
52 | Sub-Section A: SOW | 3 of 21 | 1 | South Facing, Fixed Tilt | Please Confirm the Tilt & Pitch to be considered Or Bidder is responsible for Tilt & Pitch Analysis. | Technical - Electrical | Please refer to Sl. No. 16 of Amendment-1 for SA-B: Site Specific Technical Parameters.
53 | Sub-Section A: SOW | 3 of 21 | 1 | Location Gadhi, Tehsil: Badnawar Nawapada, Rajos, Tehsil: Sarape | Please Provide the KMZ File for the Array Layout Activity Also requesting To Mark the Location of KMZ Which needs to be considered | Technical - Civil | KMZ file and geotech report are not available. Refer to Sl. No. 56 of Amendment-1. CAD file has been shared.
54 | Sub-Section A: SOW | 4 of 21 | 1 | For Operational Acceptance - 81.1% | Please confirm that this PR is bidder needs to maintained for First year or For 5 Years including O&M. | Technical - Electrical | Bidder is required to maintain OTF>1 instead of PR for Operational Acceptance, and shall provided Guaranteed Generation during O&M Period. Please refer to Sl. No. 21, 24 & 25 of Amendment-1.
55 | Sub-Section A: SOW | 6 of 21 | 3.4 | Transmission line drawings and erection plans as per DISCOM / STU / CTU guidelines | Please Confirm PSS To GSS Line is in Bidder's Scope. | Technical - Electrical | 220 kV Over Head Transmission Line / Under Ground Cable (suitable for evacuation of 200 MVA) from 33/220 kV Pooling Substation to Interconnecting Substation is in the Scope of Bidder (BoS contractor). Please refer to Clause No. 4.17 of SS-A:SOW.
56 | Sub-Section A: SOW | 8 of 21 | 4.4 | String Combiner Box (SCB) along with mounting structure in case of central inverter configuration. In case solar cables are connected to DC cable via Insulation Piercing Connector (IPC), String Isolation Box (SIB) along with mounting structure shall be provided instead of SCB | Please Confirm the Bidder needs to considered SCB Without Monitoring or SMB With Monitoring. | Technical - Electrical | Bidder is not required to provide string level monitoring, SCB level monitoring is required Please refer to Clause No. 14.1.3 of SS-B: TS-Electrical
57 | Sub-Section A: SOW | 9 of 21 | 4.1 | AC Cables (LT & HT) of appropriate size and rating along with cable termination kits, ferrules / tags, conduits, cable ties and other materials required for cable laying and termination at both the ends. | Please Confirm Maximum Fault level To be considered along with it's wit standing time. Bidder Proposed 25 kA For 1 Sec. | Technical - Electrical | The selection and rating of the AC cable, including the short circuit withstanding time, shall be within the contractor’s scope as per the system design and must comply with the overall system requirements and applicable standards.
58 | Sub-Section A: SOW | 9 of 21 | 4.11 | Inverter duty transformers of appropriate rating including fire protection system | Please Confirm Fire protection / NIFPS System to be Provided Above 10 MVA IDT Only. | Technical - Electrical | Yes, Automatic Fire Protection System (including NIFPS) to be provided for transformers above 10 MVA, as per CEA (Measures Relating to the Safety and Electric Supply), Regulations 2023. Please refer to Clause No. 35 of Amendment - 1.
59 | Sub-Section A: SOW | 9 of 21 | 4.15 | ABT meters with all necessary metering rated CTs and PTs at the plant take-off point | Please Confirm We have Considered Main & Check meters with 1 Set of Each CT PT | Technical - Electrical | OK
60 | Sub-Section B: TS-Electrical | 9 of 21 | 4.2 | Continuous operation at rated MVA on any tap with voltage variation of +/-3%, also transformer shall be capable of being loaded in accordance with IEC 60076-7 | Please confirm the name plate rating when we talk about Loading. For Example If i Choose 8.8 Mva IDT Than My Name plat rating will be 8.8 or (8.8 X 110% Overloading = 9.6 MVA Name plat rating) Please confirm. | Technical - Electrical | The nameplate rating is the transformer’s continuous rated power under specified conditions (e.g., ambient temperature, cooling, etc.) without considering overloading.
61 | Sub-Section B: TS-Electrical | 10 of 21 | 4.32 | Weather monitoring station shall include but not be limited to the following: • Pyranometers – Two in Horizontal Plane for GHI and two in inclined plane – Minimum 4 (Four) Nos. • Ultrasonic Anemometer (wind speed and direction) – 1 (one) no. • Temperature Sensor (ambient and module surface) – 5 (five) nos. • Sensors required for measurement of following parameters (i) Rainfall (mm) (ii) Relative humidity (%) • Power source to the all sensors wherever required • Data Logger | Please confirm we have to considered Qty of Sensor mentioned in the Tender or have to considered as per IEC 61724. | Technical - Electrical | Quantity of sensors shall be as per Tender document (in accordance with IEC 61724-1). Please refer to Sl. No. 27, 28, 29 & 30 of Amendment-1.
62 | Sub-Section B: TS-Electrical | 11 of 21 | 4.34 | Fire detection and fire protection system in buildings/containers, inverter / transformer yard and switchyard. | Fire detection system needs to considered for open shed type ICR also or manual call points and hotter is sufficient please confirm. | Technical - Electrical | Kindly refer to Clause No. 23 of SS-B: TS-Electrical for Fire Alarm System.
63 | Sub-Section B: TS-Electrical | 12 of 82 | 4.3 | Winding conductor shall be electrolytic grade Copper/Aluminium and insulation shall be Class F or better. | Please Confirm For Inverter Duty transformer we have to considered Aluminium Winding Or Copper Winding Please Confirm. | Technical - Electrical | Both Aluminium / Copper windings are acceptable.
64 | Sub-Section B: TS-Electrical |  | 5.21 | Installation, Testing and Commissioning of Uninterrupted Power Supply (UPS), Distribution boards, Cables, and related accessories. | Please confirm the backup time for ICR & MCR. | Technical - Electrical | 2 hours
65 | Sub-Section B: TS-Electrical | 4 of 82 | 2.1 | DC Cable SCB / IPC PCU Copper or Aluminium's/ XLPE 1.5 kV DC IS 7098 Part II | In Table It is mentioned From SCB To PCU Cable Copper or Aluminium Please confirm for bidding purpose we have to considered Aluminium Or Copper Please confirm. Also Please Confirm we have to considered Aluminium or Copper Cable For LT & HT Cable. | Technical - Electrical | Both Aluminium / Copper windings are acceptable.
66 | Sub-Section B: TS-Electrical | 23 of 82 | 5.8.1 | Bus bar shall be made of copper or aluminium with uniform cross section throughout their length | For Bidding purpose bidder is considering Aluminium Bus Bar please confirm. | Technical - Electrical | Accepted.
67 | Sub-Section B: TS-Electrical | 26 of 82 | 6 | Short circuit withstand capability as per design | Please confirm the Short circuit withstanding time needs to be considered for AC HT cable. | Technical - Electrical | The selection and rating of the AC cable, including the short circuit withstanding time, shall be within the contractor’s scope as per the system design and must comply with the overall system requirements and applicable standards.
68 | Sub-Section B: TS-Electrical | 27 of 82 | 6.8.3 | Cables within plant pooling substation shall be laid through RCC cable trench with supports | Bidder Understand RCC Cable Trench is Needed Only In PSS Area Other Cables Like DC Main, DC String & MV Cable will not be laid in RCC Cable trench it will be standard Please confirm. | Technical - Electrical | RCC cable trench is required only in the PSS area for AC/MV cables. For DC string, DC main, and other MV cables outside the PSS, standard laying methods may be adopted as per tender specifications.
69 | Sub-Section B: TS-Electrical | 33 of 82 |  | Capacity 100% UPS load for 2 hours | Please confirm same Back up time to be considered for MCR UPS also. | Technical - Electrical | Yes, backup time for MCR UPS shall also be 2 hours.
70 | Sub-Section B: TS-Electrical | 37 of 82 | 4.3 | Earth conductors buried in ground shall be laid minimum 600 mm below ground level unless otherwise indicated in the drawing. Back filling material to be placed over buried conductors shall be free from stones and harmful mixtures | In Case of hard rock area shallow depth to be considered Please confirm. | Technical - Electrical | In the case of hard rock areas, shallow burial depth for earth conductors may be considered, subject to approval by the project manager of the Employer. However, adequate mechanical protection must be provided to ensure the safety and integrity of the conductors.
71 | Sub-Section B: TS-Electrical | 37 of 82 | 11.3 | Earthing of PV Modules shall be as per the requirements of the PV Module Manufacturer | For Module to Module Earthing Bidder proposed Sareted Washer Please confirm. | Technical - Electrical | Accepted.
72 | Sub-Section B: TS-Electrical | 39 of 82 | 12.2 | Protection level for the entire plant shall be Level-III. | Bidder Proposed Level - 4 Protection For entire plant. | Technical - Electrical | The terms and conditions of the tender document shall prevail.
73 | Sub-Section B: TS-Electrical |  |  | SLD | Please Provide The PSS SLD scheme. | Technical - Electrical | SLD for interconnecting S/S Badnawar may be provided subsequently.
74 | Sub-Section B: TS-Electrical |  |  | Scada Redundancy | Please Confirm Redundancy required at MCR Level only no Redundancy Considered at ICR Level please confirm. | Technical - Electrical | Please refer to Clause No. 14.2.10 of SS-B: TS-Electrical.
75 | Sub-Section B: TS-Electrical | 41 of 82 | 14.1.3 | Web enabled Operator Dashboards: Showing key information on Generation, Performance and Current Status of various equipment in Single Line Diagram (SLD) format with capability to monitor PV array Zone level (i.e. SCB level) parameters. | In bracket it is mentioned SCB Level please confirm we have to considered SCB Mongering to SCADA. | Technical - Electrical | As per 14.1.3 String level Monitoring is not required; However, SCB level monitoring is required. Please refer to 14.1.3 of SS-B: TS-Electrical.
76 | Sub-Section B: TS-Electrical | 47 of 82 | 15.1 | Power Plant Controller (PPC) shall be provided with two processors (main processing unit and memories), one for normal operation and one as hot standby | Please confirm that we have to considered 2 PPC 1 Main + 1 Stand By As PPC Qty is mentioned as 1 in tender so please confirm the Qty Should be 2 (1 Main + 1 Stand by) | Technical - Electrical | No, it is not required to consider 2 separate PPC units. As per the tender, the PPC quantity remains 1, but it must have two processors - one main and one hot standby - as per the Clause No. 15.1 of SS-B: TS-Electrical.
77 | Sub-Section B: TS-Electrical |  |  | Reactive power Compensation | Please confirm EPC Needs to Provide SVG System For Reactive power Compensation or it is in SECI Scope. | Technical - Electrical | Reactive power Compensation is in the scope of Contractor
78 | General Annexure-I: Plant Documentation, Commissioning & Test Procedure | 16 of 20 | 6 | Battery Energy Storage System (if applicable) | Please confirm the BESS Is required in this project or not please confirm. | Technical - Electrical | BESS is not required in this project
79 | Sub-Section B: TS-Electrical |  |  | HTP | When We combined 2 in 1 Out HTP Can we used LBS On incomer Side of ICOG FYR Photo attached. | Technical - Electrical | Query not clear
80 |  |  |  |  | #VALUE! | Technical - Electrical | Query not clear
81 | Sub-Section B: TS-Electrical |  |  | GSS Coordinates | Please Provide the GSS Coordinates Along with TL Distance to considered. | Technical - Electrical | Please refer to Sl. No. 26 of Amendment-1
82 | Sub-Section B: TS-Electrical | 42 of 82 | 14.2.9 | GPS based Time Synchronization System: The SCADA system shall have a Master/Slave Clock system along with antenna, receiver, cabinet and internal interconnection cables. | Bidder Request to Considered Master GPS Clock Only At MCR Level no Slave clock required at ICR Level For time synchronization system. | Technical - Electrical | The terms and conditions of the tender document shall prevail.
83 | Sub-Section B: TS-Electrical | 42 of 82 | 14.2.10 | Configuration of Cloud server and procurement of associated subscription services shall be in the scope of the EPC Contractor. | Please confirm Life time of the subscription & Services to be considered. | Technical - Electrical | Kindly refer to Clause No. 14.2.10 for the requirement of the cloud server. The duration of the subscription and associated services shall be aligned with the O&M period of the plant, i.e., 5 years
84 | General Annexure-J: Functional Guarantee (FG) Test Procedure | 4 of 11 | 2.1.2 | Tref = Σ (𝐺𝑖,𝑘 * Tavg_mod,k ) / Σ 𝐺𝑖,𝑘 Tref PV Module temperature average over the whole day, weighted by GlobInc, i.e. | Tref temperature will be PV Module temperature derive from the PVsyst on hourly basis please confirm. | Technical - Electrical | FG Test procedure has been updated. Please refer to Sl. No. 25 of Amendment-1.
85 | General Annexure-J: Functional Guarantee (FG) Test Procedure | 5 of 11 | 2.1.4.1 | Trial Run: The PG Test for Plant Facilities shall commence with a trial run for 7 consecutive days. SECI shall estimate the PR for the Trial Run period and revert within 3 working days. Post the trial run period, the 30 days PG test will commence after communication from SECI. | Bidder request if On the trial run If minimum PR Will be achieved please considered this days in PR Test. | Technical - Electrical | Please refer to Sl. No. 25 of Amendment-1. The document has been updated as - General Annexure-J: FG Test Procedure.
86 | General Annexure-J: Functional Guarantee (FG) Test Procedure | 6 of 11 | 3 | Considering minimum 24 Nos of 15-minute time blocks to account the day for PR estimation, Daily PR shall be estimated as the average of PR calculated for 15-min time blocks falling within 99% confidence interval. | Please note that is due to grid failure or Grid Outage or weather related issue if few of the interval are missed please considered that day in PR for example 20 time block is achieved than count it in PR Day | Technical - Electrical | Please refer to Sl. No. 25 of Amendment-1. The document has been updated as - General Annexure-J: FG Test Procedure.
87 | General Annexure-J: Functional Guarantee (FG) Test Procedure | 7 of 11 |  | The test shall be repeated for 30 days in case of any outage of following equipment (as applicable) for more than 7 days. • Power Transformer/Inverter Duty Transformer • Power Conditioning Unit • HT Switchgear Panel • SCADA and data logger combined • Tilted pyranometer • Other WMS sensors | Bidder request to continue the PR after Equipment is fixed not to re-run the PR Test again for example on 8th day of pr equipment is failed an after equipment resorted PR Should be continue as 9th day not to re start the process again. | Technical - Electrical | Terms and conditions of the tender document shall prevail. Please refer to Sl. No. 25 of Amendment-1. The document has been updated as - General Annexure-J: FG Test Procedure.
88 | site visit |  |  | Transmission line passing through the acquired land. | Removing or shifting of transmission line is in scope of bidder or SECI? | Contractual | The complete RoW related to the Transmission line is in the scope of bidder, including shifting of existing line only if required.
89 | ITB | 25 of 52 | 32.4.2 (2) 3rd bullet | At the end of the e-RA, the final discount offered by the bidder, in the form of price reduction so offered on the EPC & NPV value of O&M price, shall be applied proportionately to all of the SOR Line items price (EPC Price + NPV of O&M price) quoted by the bidder initially in the financial bid. Accordingly, the revised reduced price of all of the SOR line items of the EPC & NPV of O&M will be derived. | Discounts offered by the bidder during e-RA, may not be in proportion to the SOR line items in EPC and NPV Value of O&M Price. Hence, allocation of prices to each SOR line item after the e-RA should be left to the bidder | Contractual | The terms and conditions of the tender document shall prevail.
90 | ANNEXURE TO BDS | 6 of 11 | 1.3 | The bidder should have a minimum Working Capital of INR 94,00,00,000/- (Indian Rupees Ninety-Four crores only) as per the last audited financial statement. If the bidder’s working capital is inadequate, the bidder should supplement this with a letter from the bidder’s bank, having net worth not less than INR 500 Crores, confirming availability of the line of credit for more than or equal to INR 94,00,00,000/- (Indian Rupees Ninety-Four crores only) to meet the working Capital requirement of this particular Project. | The requirement of working capital is an excessive requirement in a tender of Balance of System for Solar PV plant. All major Solar Power plant developers exclude this requirement in their tender for such projects. It is therefore requested to exclude this criteria from Qualification Requirement. | Contractual | The terms and conditions of the tender document shall prevail.
91 | GCC | 39 of 82 | 43.3.3 | At any time after the events set out in GCC Sub- Clause 43.3.1 have occurred, the Contractor may give a notice to the Project Manager/EIC requesting the issue of an Operational Acceptance Certificate in the form acceptable to the EMPLOYER in respect of the Facilities or the part thereof specified in such notice as at the date of such notice | It may be clarified that O&M Contract shall start in case of part commissioning also. The contractual terms including but not limited to payment shall apply accordingly. | Contractual | The O&M Contract shall start from the day of Operational Acceptance of the complete plant facilities.
92 | Sub-Section F: O&M Agreement | 2 of 43 | 1 | Note: Operational Acceptance of the Plant Facilities by the Employer shall be a necessary condition for signing of the O&M Agreement. The Contractor shall, however, maintain the plant facilities, in the interim period between the Plant Commissioning and the signing of the O&M Agreement |  | Contractual | Query not clear.
93 | General Annexure-J: Functional Guarantee (FG) Test Procedure | 9 of 11 | 3.2 | FOR SHORTFALL IN PR - For every 0.01 shortfall in pr below the specified pr value, liquidated damages of 1% of the contract value shall be levied. In case the plant pr shortfall is more than 0.05 below the specified pr value, then the total plant will be accepted on “as-is basis” & no payments will be made to the contractor pertaining to ‘operation acceptance’ milestone in line with the defined payment terms. Guaranteed PR shall be revised to the final PR value as determined in PR Test for the O&M period. However, any other earlier pending/running payments as may be applicable, will be paid to the contractor as usual. | LD is being levied for shortfall in performance as well as shortfall in target generation. Module being a free issue material to the bidder, request to kindly exclude this requirement from the scope of bidder. | Technical - Electrical | Liquidated Damages clause for Operational Acceptance and During O&M period have been updated. Please refer to Sl. No. 22, 24 & 25 of Amendment-1.
94 | GCC | 23 of 82 | 20.1 | Subject to Force Majeure Clause, if the Contractor fails to comply with the Time for Completion /successful commissioning or any extension thereof of Plant facilities in accordance with timelines as mentioned under the SCC, then the Contractor shall pay to the Owner a sum equivalent to half percent (0.5%) per week of the Contract Price for the whole of the facilities as liquidated damages for such default and not as a penalty, without prejudice to the Owner’s other remedies under the Contract subject to the maximum limit of five percent (05%) of Contract Price for the whole of the facilities | Request to kindly levy the LD on the amount of "uncommission" part of facilities | Contractual | Kindly refer to Amendment 01.
95 | General |  |  |  | Bidder is requested to provide the following report for reference during tender stage- 1.Tender SLD of Solar PV Plant 2.Substation SLDs 3.KMZ file 4.Existing ERT report 5.AutoCAD files 6.Topographic survey Report 7.Geotech Report | Technical - Electrical | 1. Plant SLD is in the scope of bidder, to be finalised during detailed engineering. 2. SLD to be provided subsequently. 3. Details are not available. 4. Refer to Sl. No. 56 of Amendment-1. CAD file with contour details has been shared.
96 | General |  |  |  | Bidder understand that ROW among different land parcels shall be in owner’s scope. Please clarify. | Contractual | The complete RoW is in bidder's scope.
97 | SECTION - VII SUB-SECTION A SCOPE OF WORKS_ 200 MW Dhar | 6 of 316 | 1 Project Particulars | Cumulative Power Transformer Capacity - 250 MVA (2 X 125 MVA) | Bidder understand that 2 Nos power transformer (33kV/220kV) shall be in bidder's scope. But there is contradiction in both clauses regarding the rating of power transformer. Please clarify. | Technical - Electrical | Power Transformer: 250MVA (125 x 2). Please refer to Sl. No. 17 Amendment-1
98 |  | 7 of 316 | 1 Project Particulars | Plant End Substation Power Transformer (33/220 kV) Capacity |  | Technical - Electrical | Power Transformer: 250MVA (125 x 2). Please refer to Sl. No. 17 Amendment-1
99 | SECTION - VII SUB-SECTION A SCOPE OF WORKS_ 200 MW Dhar | 6 of 316 | 1 Project Particulars | Cumulative Inverter AC Capacity - XX MVA to deliver 200MW with PF range -0.95 to +0.95 at 50°C at POI | Bidder understand that 200MW plant shall be designed with considering Inverter AC rating at 0.95 PF at 50°C. But as OEM define inverter rating at UPF at 50°C, then number of inverter may slightly increase due to the same. Please confirm. | Technical - Electrical | The inverters must collectively be capable of delivering 200 MW active power at the grid connection point at 50°C. The inverters must be capable of operating across a power factor (PF) range of -0.95 (lagging) to +0.95 (leading).
100 | SECTION - VII SUB-SECTION A SCOPE OF WORKS_ 200 MW Dhar | 6 of 316 | 1 Project Particulars | Supply of PV Modules- Supply of PV Modules at the Project Site shall be in the Scope of the Owner. The Owner shall deliver PV Modules at the Project site. However, for the purpose of bidding contractor may consider 540Wp Mono PERC module of 20.9% efficiency with dimensions 2278mm x 1134mm. | 1. Bidder understand that PV Module is not in bidder’s scope. So it is requested to share the PV module datasheet, PAN file, cable length along with module. 2. Bidder assumes that leap frog connection can be considered for module string formation. Please confirm. | Technical - Electrical | 1. Please refer to Sl. No. 16 of Amendment-1 for SA-B: Site Specific Technical Parameters. 2. PAN file of the Module shall be provided to Successful bidder. However, for the purpose of bidding contractor may consider 540Wp Mono PERC module of 20.9% efficiency with dimensions 2278mm x 1134mm. 3. Any deviation in the module supplied by Owner shall be adjusted according to Clause 32.4.2 sl no. 7. 4. The decision regarding the PV module connection configuration shall rest with the bidder; however, it must be compatible with the PV modules (Mono-PERC/TopCON/Thin Film) provided by the Owner.
101 | SECTION - VII SUB-SECTION A SCOPE OF WORKS_ 200 MW Dhar | 6 of 316 | 1 Project Particulars | Origin of Supply Items As per MNRE Order on Public Procurement (Preference to Make in India) to provide for Purchase Preference (linked with local content) in respect of RE Sector dated 9th February, 2021 and subsequent amendments | Please provide make list for the BOS equipment's. | Technical - Electrical | Bidder may propose any make subject to meeting the technical specifications.
102 | SECTION - VII SUB-SECTION A SCOPE OF WORKS_ 200 MW Dhar | 7 of 316 | 1 Project Particulars | Performance Ratio (at 220 kV side of Plant Pooling Substation) - 81.1% | As PV modules shall be provided by owner and PV module's losses contribute major factors in PR calculation. So bidder request either to provide exact losses detail, PAN file & other details of PV module. Or allow PR at the OTGT ( O&M Target Generation Test). Please confirm. | Technical - Electrical | 1. Please refer to Sl. No. 16 of Amendment-1 for SA-B: Site Specific Technical Parameters. 2. Criteria for Operational Acceptance and for O&M period have been updated. Please refer to Sl. No. 21, 24 & 25 of Amendment-1.
103 | SECTION - VII SUB-SECTION A SCOPE OF WORKS_ 200 MW Dhar | 10 of 316 | 3.11 Design and Engineering | The plant shall be capable of reactive power support in line with regulations & its amendments/clarifications. | Bidder request to clarify the scope of below item. 1. Grid Study 2. Requirement of SVG (Static VAR Generator), PMU (Phase Measuring Unit), Harmonic Filter etc. Also clarify its scope of supply, location, interconnection with CRP panel & 33kV Main Pooling switchyard, SCADA etc. | Technical - Electrical | Please refer Clause 3.9 and 3.10 of Scope of Works for Grid Study. The bidder may propose any dynamic reactive power compensation device (including SVG) to meet the requirements of CTU at the Point of Interconnection. Supply and installation of Phasor Measurement Units (PMU), and other associated equipment/accessories at the Solar Plant Pooling Substation as per CEA (Technical standard for construction of Electrical Plants & Electric Lines), Regulations, 2022 & amendments thereof is in the scope of the bidder as per Clause 4.21 of Scope of Works. Supply of harmonic filters, if required, as per the grid study is also in the scope of the bidder.
104 | SECTION - VII SUB-SECTION A SCOPE OF WORKS_ 200 MW Dhar | 12 of 316 | 4.13 Procurement & Supply | 33 kV Over Head Transmission Line / Under Ground Cable including Poles / Towers, Conductors, Insulators, Cable Termination Kits and associated accessories from 33 kV Switchgear of inverter stations to 33/220 kV Pooling Substation including Right of Way, permits and approvals. | Bidder understand that ROW, permits and approvals shall be in owner’s scope. Please clarify. | Technical - Electrical | ROW, permits and approvals shall be in the scope of Contractor. Terms and conditions of the tender document shall prevail.
105 | SECTION - VII SUB-SECTION A SCOPE OF WORKS_ 200 MW Dhar | 12 of 316 | 4.14 Procurement & Supply | 33/220 kV Solar park Substation with required number of 33 kV outdoor bays (including provision of extension on each side of the bus bar in future), required no. of 33/220 kV transformers, 220 kV Bays including Substation Automation System. Busbars, Equipment of Line Bay and Bus Coupler Bay shall be suitable for evacuation of 200 MVA. | Bidder request to provide option either to select 33kV Main HT switchgear panel at 33/220 kV Solar park Substation or 33 kV outdoor bays as per bidder requirement. | Technical - Electrical | Bidder may propose 33kV Main HT switchgear panel at 33/220 kV Solar park Substation or 33 kV outdoor bays. Please refer Clause 4.12 of Scope of Works.
106 | SECTION - VII SUB-SECTION A SCOPE OF WORKS_ 200 MW Dhar | 12 of 316 | 4.15 Procurement & Supply | ABT meters with all necessary metering rated CTs and PTs at the plant take-off point as well as at the interconnecting substation as per CEA Metering Regulations 2006 as amended time to time and state metering code. | Bidder understand that ABT meters shall only be connected at 220kV side at PSS only. ABT meter at interconnecting substation i.e., GSS shall be in owner's scope of supply. Please confirm. | Technical - Electrical | ABT meter with all necessary metering rated CTs and PTs at interconnecting substation i.e., GSS shall also be in the scope of Contractor.
107 | SECTION - VII SUB-SECTION A SCOPE OF WORKS_ 200 MW Dhar | 12 of 316 | 4.16 Procurement & Supply | Any other equipment / system required to comply with the relevant Procedures / Regulations issued by CEA/ CERC/ any other statutory body for connectivity to the Grid. | Bidder request that bidder's scope of supply is only upto 33/220 kV Solar park Substation at PSS. Further after that including 220kV TL & it's accessories, it's ROW and 220 kV bay at interconnecting substation (GSS) shall be in owner's scope. Please confirm. | Technical - Electrical | 220 kV transmission line (OHTL/UG cable) with all accessories, ROW, permits/approvals, 220 kV bay at interconnecting substation (including equipment shifting/replacement), and CTU supervision & maintenance charges shall be in the scope of the Contractor. Kindly refer to Clause No. 4.17 and 4.18 of SS-A SOW of tender document.
108 | SECTION - VII SUB-SECTION A SCOPE OF WORKS_ 200 MW Dhar | 12 of 316 | 4.17 Procurement & Supply | 220 kV Over Head Transmission Line / Under Ground Cable (suitable for evacuation of 200 MVA) including Towers, Conductors, OPGW cable, Insulators, Cable Termination Kits and associated accessories from 33/220 kV Pooling Substation to Interconnecting Substation as per CTU drawings/specifications including Right of Way, permits and approvals, CTU supervision and maintenance charges. | Bidder request that scope under this clause shall be in owner's scope. Please confirm. | Technical - Electrical | The terms and conditions of the tender document shall prevail.
109 | SECTION - VII SUB-SECTION A SCOPE OF WORKS_ 200 MW Dhar | 12 of 316 | 4.18 Procurement & Supply | 220 kV bay at interconnecting substation (suitable for evacuation of 200 MVA) as per CTU drawings/specifications including shifting or replacement of substation equipment / materials, permits and approvals, CTU supervision and maintenance charges. | Bidder request that scope under this clause shall be in owner's scope. Please confirm. | Technical - Electrical | The terms and conditions of the tender document shall prevail.
110 | SECTION - VII SUB-SECTION A SCOPE OF WORKS_ 200 MW Dhar | 13 of 316 | 4.19 Procurement & Supply | The Contractor shall provide provision to integrate Special Protection Scheme (SPS), if required, in case the RLDC requires the same. In that event, details of SPS and its setting shall be worked out in consultation with RLDC & RPC. | Bidder request that scope under this clause shall be in owner's scope. Please confirm. | Technical - Electrical | The terms and conditions of the tender document shall prevail.
111 | SECTION - VII SUB-SECTION A SCOPE OF WORKS_ 200 MW Dhar | 13 of 316 | 4.20 Procurement & Supply | Fibre Optic based communication system comprising of OPGW cable (having minimum 12 fibres) and hardware fittings for the transmission line and FOTE (STM- 16) terminal equipment, FODP, approach cables and other associated equipment/accessories at Solar Plant Pooling Substation and interconnecting substation as per CTU specifications. The communication system shall facilitate for telemetry data communication, voice communication and tele-protection. | Bidder request that scope under this clause shall be in owner's scope. Please confirm. | Technical - Electrical | The terms and conditions of the tender document shall prevail.
112 | SECTION - VII SUB-SECTION A SCOPE OF WORKS_ 200 MW Dhar | 14 of 316 | 4.20 Procurement & Supply | CCTV cameras with monitoring station along with mounting poles, power supply cables, communication cables, network switches, conduits, fittings, etc. | Bidder may mount CCTV cameras on lighting poles. Please confirm. | Technical - Electrical | Yes, the contractor may install CCTVs on lighting poles, subject to structural suitability, power availability, unobstructed view, safe maintenance access, proper cabling, and compliance with project specs. 24×7 surveillance of areas mentioned in Clause No. 22 of SS-B TS Electrical must be ensured.
113 | SECTION - VII SUB-SECTION C TECHNICAL SPECIFICATIONS (TS)- CIVIL | 111 Of 316 | 2 Topographical Survey | The Contractor shall carry the Bench Mark from nearest GTS Bench mark or any other established source like Railway station, Permanent PWD/ WRD structure etc. | Bidder is requested to identified and provide the Permanent bench mark as reference near each site location to establish the bench mark at project site by bidder. Please confirm. | Technical - Civil | This shall be in the scope of the EPC Contractor. Terms and conditions of tender shall prevail.
114 | SECTION - VII SUB-SECTION C TECHNICAL SPECIFICATIONS (TS)- CIVIL | 112 Of 316 | 2 Topographical Survey | Positions, both in plan and elevation, of all natural and artificial features in the area like waterways, railway tracks, trees, cultivation, houses, fences, pucca and kutcha roads including culverts and crossings, foot tracks, other permanent objects like telephone posts and transmission towers etc. are to be established and subsequently shown on survey maps by means of conventional symbols (preferably symbols of survey of India Maps). | Bidder understanding is that the allotted plot of proposed solar project shall be free from all obstacle like electricity poles, transmission towers waterways, railway tracks & trees etc. Topographic survey shall be carried out as per the standard practice. | Technical - Civil | Refer to Sl. No. 56 of Amendment-1. CAD file has been shared. Topographical Survey needs to be carried out as per the terms & conditions of the tender.
115 | SECTION - VII SUB-SECTION C TECHNICAL SPECIFICATIONS (TS)- CIVIL | 114 Of 316 | 3 Geotechnical Investigations 3.8 | However, minimum grade of concrete shall be as specified under Cl.Error! Reference source not found concrete works. | Please specify the minimum grade of concrete. | Technical - Civil | Refer to Sl. No. 8 of Amendment-1.
116 | SECTION - VII SUB-SECTION C TECHNICAL SPECIFICATIONS (TS)- CIVIL | 117 Of 316 | 5 Area Grading and Land Development 5.1 | The Finished Grade Level (FGL) of the proposed plant shall be fixed with reference to the highest flood level (HFL) and surrounding ground profile at proposed site to avoid flooding of plant site. | Bidder is requested to provide HFL & the existing Finish Graded level at the proposed site location. | Technical - Civil | This shall be in the scope of the EPC Contractor. Terms and conditions of tender shall prevail.
117 | SECTION - VII SUB-SECTION C TECHNICAL SPECIFICATIONS (TS)- CIVIL | 118 Of 316 | 6 Area Grading and Land Development 5.4 | The contractor is responsible for making the site ready and easily approachable by clearing bushes, felling of trees (mandatory permissions/ licenses/ statutory clearances from competent authorities if required for cutting of trees, blasting or mining operations, disposal of waste material etc. Shall be obtained by the contractor), cutting, filling with selected excavated earth or borrowed earth including identifying borrow areas. | Bidder understanding is that No Major site Grading and Levelling is in the scope of Bidder except micro levelling.Also,Bidder is requested to provide the location from where earth material is to be borrowed for land development and filling purpose. | Technical - Civil | This shall be in the scope of the EPC Contractor. Terms and conditions of tender shall prevail.
118 | SECTION - VII SUB-SECTION C TECHNICAL SPECIFICATIONS (TS)- CIVIL | 118 Of 316 | 7 Area Grading and Land Development 5.6 | Excess earth, if any, shall be disposed of properly at location as directed by the Engineer. | Please provide the lead distance for disposal of waste material. | Technical - Civil | This shall be in the scope of the EPC Contractor. Terms and conditions of tender shall prevail.
119 | SECTION - VII SUB-SECTION C TECHNICAL SPECIFICATIONS (TS)- CIVIL | 121 Of 316 | 7 Surface/ Area drainage 7.5 | The coefficient of run-off for estimation of design discharge shall be considered as per catchment characteristics, however it shall not be less than 0.6. | The Bidder Proposes that the coefficient of run-off shall be as per IRC / hydrology report recommendation. | Technical - Civil | Accepted subject to min value of 0.6 specified as per TS
120 | SECTION - VII SUB-SECTION C TECHNICAL SPECIFICATIONS (TS)- CIVIL | 121 Of 316 | 7 Surface/ Area drainage 7.6 | The drainage scheme shall be designed considering the plant plot area and the surrounding catchment area contributing to the plant area drainage as per the topography. | Kindly provide the percent of catchment area to be considered. | Technical - Civil | The terms and conditions of the tender document shall prevail.
121 | SECTION - VII SUB-SECTION C TECHNICAL SPECIFICATIONS (TS)- CIVIL | 121 Of 316 | 7 Surface/ Area drainage 7.8 | Suitable size plant peripheral drain as per design and requirement (min. 450mm wide x 450mm deep) along inside of plant boundary wall/ fence shall be provided for smooth channelization of outside storm water and to avoid flooding in the plant. | The Bidder proposes that drain will be provided where ever required but not all along the periphery of site. Bidder Understanding is that drain is provided along the internal road only .please specify. Also, We request kindly to provide the locations and invert level of drain outfall in-order to plan the drain layout & design with respect to the requirements for the intended Solar Park. | Technical - Civil | Peripheral drain requirement shall be as per the topographical considerations. Terms and conditions of tender shall prevail.
122 | SECTION - VII SUB-SECTION C TECHNICAL SPECIFICATIONS (TS)- CIVIL | 122 Of 316 | 8 Surface/ Area drainage 7.12 | The drain outfall shall be connected to the nearest existing natural drain(s)/ water body outside plant premises and it shall be ensured that the drainage water shall not re-enter the plant nor encroach/ flood in the adjacent property/ plot. | Please Provide the availability of the Existing Natural drains/ water Body outside the Plant and its distance from the plant. | Technical - Civil | This shall be in the scope of the EPC Contractor. Terms and conditions of tender shall prevail.
123 | SECTION - VII SUB-SECTION C TECHNICAL SPECIFICATIONS (TS)- CIVIL | 124 Of 316 | 10 Design Loads 10.2 | The following minimum imposed load as indicated for some of the important areas shall, however be considered for the design. | The Bidder proposes that the Imposed (Live) loads are to be considered as per IS 875 (Part-II) instead of the mentioned imposed loads. | Technical - Civil | The terms and conditions of the tender document shall prevail.
124 | SECTION - VII SUB-SECTION C TECHNICAL SPECIFICATIONS (TS)- CIVIL | 124 Of 316 | 11 Design Loads 10.4 | Basic wind speed (Vb) at project site shall be taken as per IS 875 (part-3) unless otherwise specified elsewhere. | Bidder is requested to provide basic wind speed of proposed area. | Technical - Civil | Refer 'Sub Section A: Scope of Works' of Section VII.
125 | SECTION - VII SUB-SECTION C TECHNICAL SPECIFICATIONS (TS)- CIVIL | 125 Of 316 | 10 Design Loads 10.10.1 | The bidder shall conduct wind tunnel studies for the design and analysis of complete MMS. | Bidder is requested to provide wind tunnel studies for bidding purpose. and conducting the wind tunnel studies same will be in the scope of SECI please confirm. | Technical - Civil | Wind tunnel study shall be in the scope of the EPC Contractor. Refer Sl No.2 of Amendment 1.
126 | SECTION - VII SUB-SECTION C TECHNICAL SPECIFICATIONS (TS)- CIVIL | 133 Of 316 | 15 Module Mounting Structure (MMS) 13.14 | 13.14 The vertical diagonal bracing shall be provided in end spans and every alternate span for all rows of columns of each unit (table) of MMS. | Bidder propose vertical diagonal bracing shall be as per provided based on the design since it is required to control overall deflection of the structure within permissible limits and it also depends upon table configuration which will be finalized during detailed design. | Technical - Civil | Refer to Sl. No. 6 of Amendment-1.
127 | SECTION - VII SUB-SECTION C TECHNICAL SPECIFICATIONS (TS)- CIVIL | 134 Of 316 | 14 Module Mounting Structure (MMS) 13.24 | Min. diameter of bolt for MMS connections shall be 10mm (12 mm in case of single bolt connection) except at column-rafter connection, where it shall not be less than 12mm (not less than 16mm in case of single bolt connection). | Minimum diameter of bolt for MMS connections shall be provided as per the design requirement of the structure. Please confirm. | Technical - Civil | The terms and conditions of the tender document shall prevail.
128 | SECTION - VII SUB-SECTION C TECHNICAL SPECIFICATIONS (TS)- CIVIL | 137 Of 316 | 16.2 Functional requirements | 16.2.1 MCR Buildings | Please provide GA & Architectural view & approx. size/area of MCR building for bidding purpose. | Technical - Civil | This shall be in the scope of the EPC Contractor. Terms and conditions of tender shall prevail.
129 | SECTION - VII SUB-SECTION C TECHNICAL SPECIFICATIONS (TS)- CIVIL | 139 Of 316 | 16.2 Functional requirements | 16.2.3 Storage cabin for plant Spare | Please specify the approx. size/ area of storage cabin required along with architectural features for bidding purpose. | Technical - Civil | Size of storage cabin shall be finalized during detailed engineering as per the functional requirement.
130 | SECTION - VII SUB-SECTION C TECHNICAL SPECIFICATIONS (TS)- CIVIL | 144 Of 316 | 21. Plinth filling for buildings | Plinth beam, when provided, shall be taken minimum 200mm below FGL. The plinth filling below Ground floor (GF) for all buildings shall be provided with following specifications. (i) Well compacted sub-grade (ii) Well compacted boulder soling with interstices filled with sand over compacted sub-grade. (iii) 75mm thick PCC 1:3:6 over (ii) (iv) 100mm thick PCC 1:2:4 over (iii) (v) 40mm thick floor finish over (iv) | The Bidder Proposes that the filling will be- 1).75mm mm thick PCC laid over well compacted 75mm well grades brick ballast base. | Technical - Civil | The terms and conditions of the tender document shall prevail.
131 | SECTION - VII SUB-SECTION C TECHNICAL SPECIFICATIONS (TS)- CIVIL | - | GENERAL | - | Please provide seismic zone for proposed area. | Technical - Civil | Refer 'Sub Section A: Scope of Works' of Section VII.
132 | SECTION - VII SUB-SECTION C TECHNICAL SPECIFICATIONS (TS)- CIVIL | - | GENERAL | - | Bidder is requested to provide the detail technical specification of culvert. | Technical - Civil | Refer Cl 6.7 (Page 14 of 58) of TS.
133 | SECTION - VII SUB-SECTION C TECHNICAL SPECIFICATIONS (TS)- CIVIL | - | GENERAL | - | Bidder is requested to provide the following report for reference during tender stage- 1. Existing Site investigation Report. 2. Existing Topography survey. 3. Existing Geotechnical investigation. 4. Existing layout & drawings of Roads & Drainage for better understanding. | Technical - Civil | Details sought as per Sl no.1, 3 & 4 are not available. For Sl no. 2, refer to Sl. No. 56 of Amendment-1. CAD file has been shared.
134 | SECTION - VII SUB-SECTION C TECHNICAL SPECIFICATIONS (TS)- CIVIL | - | GENERAL | - | No major tree cutting is envisaged in bidder’s scope other than minor site clearance and removal of shrubs, vegetation required for establishment of a solar park. Please confirm. | Technical - Civil | The terms and conditions of the tender document shall prevail.
135 | SECTION - VII SUB-SECTION C TECHNICAL SPECIFICATIONS (TS)- CIVIL | - | GENERAL | - | Bidder is requested to specify the Grade of concrete, Reinforcement steel & Structural steel used for construction. | Technical - Civil | The terms and conditions of the tender document shall prevail.
136 | SECTION - VII SUB-SECTION C TECHNICAL SPECIFICATIONS (TS)- CIVIL | - | GENERAL | - | Bidder presume that all statutory clearances shall be provided by the owner. However, bidder shall assist to provide the necessary documents for the same. | Contractual | The process for obtaining any statutory clearances (if required) will be in the scope of bidder. However, at all the stage SECI and the state government will provide assistance in getting the necessary approvals.
137 | SECTION - VII SUB-SECTION C TECHNICAL SPECIFICATIONS (TS)- CIVIL | - | GENERAL | - | Construction Power and Construction Water availability at site to be made to the contractor. | Technical - Civil | The terms and conditions of the tender document shall prevail.
138 | SECTION - VII SUB-SECTION C TECHNICAL SPECIFICATIONS (TS)- CIVIL | - | GENERAL | - | Site Security shall be in the scope of the Owner. | Contractual | The terms and conditions of the tender document shall prevail.
139 | SECTION - VII SUB-SECTION C TECHNICAL SPECIFICATIONS (TS)- CIVIL | - | GENERAL | - | Owner to provide well graded and levelled land within the vicinity of the site for Contractor Site Office establishment, labour hutment & Storage Space free of cost to the Bidder. Please confirm. | Contractual | Grading and Levelling of land is under BoS Contractor's scope.
140 | SECTION - VII SUB-SECTION C TECHNICAL SPECIFICATIONS (TS)- CIVIL | - | GENERAL | - | While carrying out construction activities below ground level, if we meet any obstruction e.g. presence of any drainage pipe / water or fire pipeline, cable / ash trench, any leftover foundation concrete, live wire etc., the owner shall arrange to remove the same & we shall be freed by the owner from any such obstruction for conducting our works. Please confirm | Contractual | Any such cases if arrived during the construction stage, must be handled by BoS Contractor in mutual consultation with the Project Manager.
141 | SECTION - VII SUB-SECTION C TECHNICAL SPECIFICATIONS (TS)- CIVIL | - | GENERAL | - | Please confirm if any ground improvement is required at the site. Kindly share the preliminary geotechnical investigation report with expert recommendations of SBC during tender stage. | Technical - Civil | Geotech report is not available; Detailed investigation is in the scope of the EPC Contractor
142 | GCC | 100 of 264 | 1.1.48 | NTP means Notice to Proceed subsequent to the placement of LOA/NOA/LOI. NTP will be issued by the owner within a maximum time frame of 90 days from the date of LOA/NOA/LOI, failing which the LOA/NOA/LO shall stand withdrawn without creating any further liability on either party. In such case EMD/PBG, as applicable submitted by the contractor shall be released. | In the event issuance of NTP has been delayed for the reasons not attributable to the Bidder and the Owner withdraws LOA/NOA - Whether the Bidder will be entitled to appropriate compensation ? | Contractual | NTP will not be applicable in this case and all the contractual obligations will start from the date of signing of Contract Agreement as mentioned in the SCC section of the tender document.
143 | GCC | 112 of 264 | 20.3 | The Owner may by giving (01) one-month notice to the Contractor cancel the Contract without prejudice to the Owner’s right under Clauses 20.1 and 20.2 or any other provisions contained in the Contract to determine the Contract and claim damages from the Contractor. | Clause 20.1 and 20.2 talks about liquidated damages which is equivalent to half percent (0.5%) per week of the Contract Price and subject to capping of 5% of the Contact Price. | Contractual | Query not clear.
144 | GCC | 122 of 264 | 32.1.2 | The Contractor shall acquire, on behalf of Owner, in the Owner’s name, all permits, approvals and/or licenses from all local, state or national government authorities or public service undertakings in the Country/State where the Site is located that are necessary for the setting up of the Plant & operation of Plant till its desired life as mentioned under the Contract, including, but not limited to, entry permits for all imported Owner’s/EMPLOYER’s Equipment (if any). In this regard, any document required from Owner/ EMPLOYER shall be intimated at least 10 days prior to submission. Contractor has to ensure safe keeping of the documents and diligent use. It is the responsibility of the Contractor to safe keep and return all the original approvals, permits, licenses, certificates and other relevant document generated as a result of the setting up of project and comprehensive O&M process to the Owner. | Please clarify as to whether the Contractor is also required to bear cost while taking such permits and approvals in the name of Owner. | Contractual | All such cases will be dealt on case to case basis. The process for obtaining any statutory clearances (if required) will be in the scope of bidder. However, at all the stage SECI and the state government will provide assistance in getting the necessary approvals.
145 | SCC | 179 of 264 | 15 | Supply and Services payment terms: (iv) Final Ten percent (10%) payment of Supplies shall be paid against submission of the BG of the equivalent amount & against the Operational Acceptance of the plant Facility pursuant to successful Guarantee Tests and demonstration of Performance Ratio (PR) including submission of all as-built drawings and O&M manual. This BG shall be valid for a period of 18 (Eighteen) months from the date of its issuance & will be released after CUF demonstration on completion of first year of O&M, pursuant to the submission of all requisite documentation up to the final acceptance of the Plant facilities. However, in case of any delay, the BG shall be extended suitably | If the EPC contractor has completed all supplies and plant has been commissioned in accordance with SECI standards, the corresponding payment should be released upon Operational Acceptance. Operational Acceptance should be deemed achieved upon successful completion of the performance test, meeting all conditions outlined in Clause 43.3.2 of the GCC, and not be linked to Final Takeover, which is scheduled one year after Operational Acceptance. If the intent of this clause is solely to safeguard SECI against any potential issues, it is important to note that the existing 5% Performance Bank Guarantee (PBG) already serves this protective purpose. | Contractual | The terms and conditions of the tender document shall prevail.
146 | Sub-Section A: SOW | 6 of 316 | 1 | Project Particulars | Please provide the PV Module data sheet or if PV Module data sheet is not available please provide the losses to be considered for evaluation during bidding stage. This will enable all Bidders to consider similar PV Module specifications. | Technical - Electrical | Please refer to Sl. No. 16 of Amendment-1 for SA-B: Site Specific Technical Parameters.
147 | General Annexure-J: Functional Guarantee (FG) Test Procedure | 264 of 316 | 3 | FOR SHORTFALL IN PR - For every 0.01 shortfall in pr below the specified pr value, liquidated damages of 1% of the contract value shall be levied. In case the plant pr shortfall is more than 0.05 below the specified pr value, then the total plant will be accepted on “as-is basis” & no payments will be made to the contractor pertaining to ‘operation acceptance’ milestone in line with the defined payment terms. FOR SHORTFALL IN TARGET GENERATION – Liquidated damages of amount equal to the NPV of the estimated shortfall in cash flow resulting over the period of 25 years due to shortfall in actual generation against target generation, calculated at a tariff of Rs. 2.57 per unit (kWh) and discount rate of 6.8% shall be levied. | We seek clarification regarding the rationale behind the provision for dual Liquidated Damages (LD) during the performance test. In general practice, particularly in BOS bids issued by other PSUs, there is a provision for an Output Target Generation Test (OTGT), wherein the EPC contractor is required to meet or exceed a specified generation target. In such cases, LD is applicable only if the generation guarantee is not met during the O&M period (i.e., typically after one year or beyond), and there is no LD imposed during the performance test conducted immediately after commissioning. We request you to kindly clarify the need for LD at both stages in this context. | Technical - Electrical | Liquidated Damages clause for Operational Acceptance and During O&M period have been updated. Please refer to Sl. No. 22, 24 & 25 of Amendment-1.
148 | General |  |  | Plant Layout | Please provide the AutoCAD & ,kmz file of the plant with clear boundary demarcations. | Technical - Civil | KMZ file is not available. Refer to Sl. No. 56 of Amendment-1. CAD file has been shared.
149 | General |  |  | Site Studies | Please provide us the Geotech, Hydro or Topo reports for the project enable us to access the risks. | Technical - Civil | Topographical Survey Report has been shared for reference. Other reports are not available.
150 | Annexure to BDS - QR | 83 | III A | The Bidder should have executed an Industrial project either as developer or as EPC Contractor in the area of Power/ Steel/ Oil and Gas/ Petro-Chemical/ Fertilizer/Cement/Coal mining including Coal handling plant/Infrastructure and/ or any other process industry, of a value of INR 187 Crores or more in a single project or single work or above in last seven years and till last date of bid submission. However, such project capacity must have been in satisfactory operation for at least six (06) months prior to the last date of bid submission. | In case of RE Power sector, as per the industry practice for Wind Power Projects, the EPC Contract is awarded excluding supply and installation work of WTGs scope - due to commercial reasons. Hence we presume that a RE power project executed by Wind EPC Contractor having scope except the WTG supply and installation work, technically qualifies under this clause. Please confirm. | Contractual | No
151 | Annexure to BDS - QR | 83 | III A | The Bidder should have executed an Industrial project either as developer or as EPC Contractor in the area of Power/ Steel/ Oil and Gas/ Petro-Chemical/ Fertilizer/Cement/Coal mining including Coal handling plant/Infrastructure and/ or any other process industry, of a value of INR 187 Crores or more in a single project or single work or above in last seven years and till last date of bid submission. However, such project capacity must have been in satisfactory operation for at least six (06) months prior to the last date of bid submission. | What kind of documentation or certificate needs to be provided to confirm the qualification under this financial criteria of Industrial project having INR 187 crores value . Will a CA certificate stating the contract amounts and invoiced amounts against contract be sufficient ? Please advise | Contractual | The list of projects commissioned at least 6 months prior to the last date of Bid Submission, indicating whether the project is grid connected, along with a scanned copy of the Commissioning certificate and Work order / Contract / Agreement/LOI from the Client (or Owner) shall be submitted
152 | VI | 184 | All | Sample forms & Formats | Can the editable word file of each format be provided? | Contractual | No.
153 | VII |  |  | General | We presume that the Solar Land is / will be acquired by SECI and the same will be free from any encumbrance's and ROW issues. | Contractual | The complete land parcel is under SECI's name and the RoW in under bidder's scope. However, SECI will ensure encumbrance land.
154 | VII - A | 12 | 4.17 | 220 kV Over Head Transmission Line | Is there any tentative route proposed for EHV line and also the approved tower design shall be as per PGCIL approved designs or any other approved design to be used ? | Technical - Electrical | RoW for Transmission line is in the scope of the bidder. Tower design shall be as per PGCIL approved designs
155 | VII - A | 12 | 4.18 | 220 KV Bay | Require approved Bay drawings. Also is 220 KV Bay is AIS or GIS - please clarify | Technical - Electrical | 220 kV Bay is AIS. Bidder shall collect approved Bay drawings from the STU.
156 | VII - B | 34 | 3.7.2 | Reactive Power control | Dynamic Reactive power compensation as per CTU guiltiness shall be acceptable through Inverter-PCU/Capacitor/Reactor or SVG is mandatory requirement? | Technical - Electrical | Dynamic Reactive power compensation as per CTU guidelines shall be acceptable through Inverter-PCU/Capacitor/Reactor/ SVG. However, PCU shall also be capable of providing reactive power compensation.
157 |  |  |  | General | Is there any approved vendor list. Same may please be shared | Technical - Electrical | There is no approved vendor list.
158 | VII - B | 101 | 22.1 | CCTV Camera | Is there any requirement of CCTV camera monitoring along periphery boundary of plant | Technical - Electrical | Kindly refer to Clause No. 22.1 for areas to be covered by CCTV.
159 |  | 2 | SA-A | Tentative Land Layout with Contour Details | Please share the KMZ file of Land Parcel | Technical - Civil | KMZ file is not available. Refer to Sl. No. 56 of Amendment-1. CAD file has been shared.
160 | VII - A | 18 | 6.19 | General | ROW and Land development of approach road is in bidder scope or SECI scope - please clarify | Technical - Civil | Yes, the Right of Way (ROW) and land development of the approach road is in the bidder's scope. Terms and conditions of tender shall prevail.
161 | SECTION - II INSTRUCTION TO BIDDERS (ITB) | 41 / 264 | i. Contract Price Adjustment due variation in the offered PV module: | #VALUE! | Bidder would like to clarify that the module efficiency is completely dependent on the Wp and dimension of the module. So based on the dimension of the modules, same 540 Wp modules of different manufacturers may have slight variation in efficiency. So, 540 Wp modules of two different manufacturers with different efficiencies will not have impact on the BoS cost and the BoS will be same for the bidder for 540 Wp modules with different efficiencies. But as per the stated formula the contract price will have implication. So, bidder request to remove the formula based on efficiency and reframe the formula accordingly with change in module Wp capacity instead of change in module efficiency. | Contractual | The formula for Adjustment in BoS cost has been derived on the basis of change in BoS cost (corresponding to change in land requirement, concrete cost, excavation cost, DC Cable cost and MMS cost) with respect to the variation in module efficiency provided to the Contractor. Further it is to be clarified that the Module dimensions and Wattage corresponding to the particular Module technology has also been considered as input parameter in order to arrive at the formula for adjustment while comparing with the reference Module type.
162 | III - BID DATA SHEETS (BDS) | 68 / 264 | 7 | 16.11 The EMD can also been submitted in the from of Surety Bond towards EMD as per Format F-31 of the Sample Forma and Format Section of the tender document. | Bidder understands that the submission of Insurance Surety Bonds are allowed for EMD. Please clarify. | Contractual | Yes
163 | IV - GENERAL CONDITIONS OF CONTRACT (GCC) | 108 / 264 | 14.1 | Extension of Time for Commissioning: The time for Project commissioning as specified in the SCC is firm & final binding till the final commissioning of the Plant facilities. The Time(s) for Commissioning specified in the SCC shall be extended if the Contractor is delayed or impeded in the Performance of any of its obligations under the Contract due to delay in fulfilment of obligations by the Owner or by the reason of any of occurrence of Force Majeure as provided in the Tender for Force Majeure. | Bidder request to modify the clause as follows, The time for Project commissioning as specified in the SCC is firm & final binding till the final commissioning of the Plant facilities. The Time(s) for Commissioning specified in the SCC shall be extended if the Contractor is delayed or impeded in the Performance of any of its obligations under the Contract due to delay in fulfilment of obligations by the Owner or by the reason not attributable to the Contractor or by the reason of any of occurrence of Force Majeure as provided in the Tender for Force Majeure. | Contractual | The terms and conditions of the tender document shall prevail.
164 | IV - GENERAL CONDITIONS OF CONTRACT (GCC) | 108 / 264 | 14.1 | Extension of Time for Commissioning: The time for Project commissioning as specified in the SCC is firm & final binding till the final commissioning of the Plant facilities. The Time(s) for Commissioning specified in the SCC shall be extended if the Contractor is delayed or impeded in the Performance of any of its obligations under the Contract due to delay in fulfilment of obligations by the Owner or by the reason of any of occurrence of Force Majeure as provided in the Tender for Force Majeure. | If the Project commissioning is getting delayed because of any of the reasons not attributable to the contractor, bidder request to add the clause that payment related to commissioning and operational acceptance of the plant to be released against the submission of equivalent BG. Please accept. | Contractual | The clause mentioned in GCC is general in nature and all case will be dealt on case to case basis in line with the terms and conditions of the tender document.
165 | IV - GENERAL CONDITIONS OF CONTRACT (GCC) | 108 / 264 | 14.1 | Extension of Time for Commissioning: The time for Project commissioning as specified in the SCC is firm & final binding till the final commissioning of the Plant facilities. The Time(s) for Commissioning specified in the SCC shall be extended if the Contractor is delayed or impeded in the Performance of any of its obligations under the Contract due to delay in fulfilment of obligations by the Owner or by the reason of any of occurrence of Force Majeure as provided in the Tender for Force Majeure. | Bidder request to add the following clause also under Extension of Time, "If any statutory approval or commissioning related approvals are getting delayed which is not under the control of the contractor" due extension of time equivalent to the delay will be provided to the contractor | Contractual | The terms and conditions of the tender document shall prevail.
166 | IV - GENERAL CONDITIONS OF CONTRACT (GCC) | 111 / 264 | 19.3 | Force Majeure | The following to be added at the end of this clause “19.3 Notwithstanding anything stated herein, the provisions of this clause shall not apply to the Employer’s payment obligations towards the Contractor” | Contractual | The terms and conditions of the tender document shall prevail.
167 | IV - GENERAL CONDITIONS OF CONTRACT (GCC) | 112 / 264 | 19.7 | If works are suspended by Force Majeure conditions lasting for more than two months, the EMPLOYER/Owner shall have the option of cancelling this Contract in whole or part thereof, at its discretion. | Bidder request to modify the clause as follows, If works are suspended by Force Majeure conditions lasting for more than two months, the EMPLOYER/Owner or the contractor shall have the option of cancelling this Contract in whole or part thereof, by giving notice to the other party. | Contractual | A prior notice will be served by the owner in all such cases.
168 | IV - GENERAL CONDITIONS OF CONTRACT (GCC) | 112 / 264 | 19.8 | The Contractor will not be entitled to claim any compensation for Force Majeure conditions and shall take appropriate steps to insure its men and materials utilized by it under the Contract. | Bidder request to modify the clause as follows, The Contractor will be entitled to claim reasonable compensation for Force Majeure conditions and shall take appropriate steps to insure its men and materials utilized by it under the Contract. | Contractual | The terms and conditions of the tender document shall prevail.
169 | IV - GENERAL CONDITIONS OF CONTRACT (GCC) | 112 / 264 | 20.1 | Subject to Force Majeure Clause, if the Contractor fails to comply with the Time for Completion /successful commissioning or any extension thereof of Plant facilities in accordance with timelines as mentioned under the SCC, then the Contractor shall pay to the Owner a sum equivalent to half percent (0.5%) per week of the Contract Price for the whole of the facilities as liquidated damages for such default and not as a penalty, without prejudice to the Owner’s other remedies under the Contract subject to the maximum limit of five percent (05%) of Contract Price for the whole of the facilities. | Bidder request to modify the clause as follows as per the standard industry practice, Subject to Force Majeure Clause, if the Contractor fails to comply with the Time for Completion /successful commissioning or any extension thereof of Plant facilities in accordance with timelines as mentioned under the SCC, then the Contractor shall pay to the Owner a sum equivalent to half percent (0.5%) per week of the Contract Price for the uncommissioned portion of the facilities as liquidated damages for such default and not as a penalty, without prejudice to the Owner’s other remedies under the Contract subject to the maximum limit of five percent (05%) of Contract Price for the whole of the facilities. | Contractual | Kindly refer to Amendment 01.
170 | IV - GENERAL CONDITIONS OF CONTRACT (GCC) | 112 / 264 | 21.1 | 21.1 Whenever any claim against the Contractor for the payment of a sum of money arises out of or under the Contract, the Contractor shall pay to the Owner on demand any balance remaining due to the Owner shall be entitled to recover such sum by appropriating in part or whole from the Contract Performance Security of the Contractor. In the event of the security being insufficient or if no security has been taken from the Contractor, then the balance or the total sum recoverable, as the case may be shall be deducted from any sum then due or which at any time thereafter may become due to the Contractor. | Bidder requests that all claims of the Employer shall be notified to the Contractor not later than 28 days from the date such claim arises and the parties shall need to amicably agreed on the amount payable by the Contractor. In the event the parties are unable to reach a consensus, the claims of the Owner shall be referred to dispute resolution process. Therefore, the agreed/undisputed claims of the Owner shall only be recovered from the RA Bills or forfeiture of the Performance Security. please confirm | Contractual | The terms and conditions of the tender document shall prevail.
171 | IV - GENERAL CONDITIONS OF CONTRACT (GCC) | 114 / 264 | 24 | The Contract Performance Security shall be in the form of either Banker’s Cheque or Demand Draft or Bank Guarantee and shall be in the currency of the Contract and will be issued in the name of the Owner as specified in the SCC. | Bidder request to modify as follows, The Contract Performance Security shall be in the form of either Banker’s Cheque or Demand Draft or Bank Guarantee or Insurance Surety Bond and shall be in the currency of the Contract and will be issued in the name of the Owner as specified in the SCC. | Contractual | Kindly refer to SCC section. Insurance Surety Bond for EMD and PBG submission is accepted.
172 | IV - GENERAL CONDITIONS OF CONTRACT (GCC) | 115 / 264 | 25.1.2 (a) | cease all further supply, except for such supply as the Owner may specify in the notice of termination for the sole purpose of protecting that part of the supplies already executed, or any supply required to leave the Site in a clean and safe condition | Bidder request to modify as follows, cease all further supply, except for such supply already in transit and except for such supply already manufacturing has commenced and except for such supply as the Owner may specify in the notice of termination for the sole purpose of protecting that part of the supplies already executed, or any supply required to leave the Site in a clean and safe condition | Contractual | The terms and conditions of the tender document shall prevail.
173 | IV - GENERAL CONDITIONS OF CONTRACT (GCC) | 117 / 264 | 25.2.4 (a) | cease all further supply, except for such supply as the Owner may specify in the notice of termination for the sole purpose of protecting that part of the supplies already executed, or any supply required to leave the Site in a clean and safe condition | Bidder request to modify as follows, cease all further supply, except for such supply already in transit and except for such supply already manufacturing has commenced and except for such supply as the Owner may specify in the notice of termination for the sole purpose of protecting that part of the supplies already executed, or any supply required to leave the Site in a clean and safe condition | Contractual | The terms and conditions of the tender document shall prevail.
174 | IV - GENERAL CONDITIONS OF CONTRACT (GCC) | 122 / 264 | 32.1.2 | The Contractor shall acquire, on behalf of Owner, in the Owner’s name, all permits, approvals and/or licenses from all local, state or national government authorities or public service undertakings in the Country/State where the Site is located that are necessary for the setting up of the Plant & operation of Plant till its desired life as mentioned under the Contract, including, but not limited to, entry permits for all imported Owner’s/EMPLOYER’s Equipment (if any). | Bidder's understanding is that bidder is required to take the permits and approvals and/or licenses for only the scope of works allocated for the bidder. As the project developer is SECI all other project related approvals will be taken care by SECI. Please clarify. | Contractual | The process for obtaining any statutory clearances (if required) will be in the scope of bidder. However, at all the stage SECI and the state government will provide assistance in getting the necessary approvals.
175 | IV - GENERAL CONDITIONS OF CONTRACT (GCC) | 122 / 264 | 32.1.3 | In the matter of connectivity of Plant to DISCOM’s substation, the Owner will take the necessary connectivity permission, however, all the other permissions and clearances as deemed required by the State Agency/DISCOM for Bay allocation, technical/regulatory compliance for interconnection, ROW etc are to be taken by the Contractor. | As the connectivity is obtained by the employer bidder request to consider all the other permissions and clearances as deemed required by the State Agency/DISCOM for Bay allocation, technical/regulatory compliance for interconnection, ROW etc in employer's scope. | Contractual | The process for obtaining any statutory clearances (if required) will be in the scope of bidder. However, at all the stage SECI and the state government will provide assistance in getting the necessary approvals.
176 | IV - GENERAL CONDITIONS OF CONTRACT (GCC) | 122 / 264 | 32.1.4 | The Contractor shall acquire in its name all permits, approvals and/or licenses from all local, state or national government authorities or public service undertakings in the country where the Site is located that are necessary for the Performance of the Contract, including, but not limited to, the right of way for the access to site and for erection of transmission lines as applicable, visas for the Contractor’s and Sub-Contractor’s personnel and entry permits for all imported Contractor’s Equipment. | As the land for the project is provided by the employer bidder request to consider the right of way for the access to site and for erection of transmission lines as applicable in the scope of employer. | Contractual | The RoW is in bidder's scope.
177 | IV - GENERAL CONDITIONS OF CONTRACT (GCC) | 122 / 264 | 32.1.4 | The Contractor shall acquire in its name all permits, approvals and/or licenses from all local, state or national government authorities or public service undertakings in the country where the Site is located that are necessary for the Performance of the Contract, including, but not limited to, the right of way for the access to site and for erection of transmission lines as applicable, visas for the Contractor’s and Sub-Contractor’s personnel and entry permits for all imported Contractor’s Equipment. | It is requested to confirm the status of all the project related approvals for commencement of the works. Bidder assumes that all the project approvals shall be obtained by the Employer including but not limited all government/statutory approvals in relation to the project shall be obtained by Employer (including Construction Permit, Forest clearances/ defence approvals- if any, grant of land/encumbrance and hindrance-free allocation where site is located). Contractor shall be responsible for statutory approvals necessary for engagement of his workmen at site only. In the event of delay by the Employer, then the Employer shall grant suitable extension of time for the execution of the work and adjustment in the contract price along with cost compensation for such delays. Bidder also requests that all statutory approvals shall be obtained by Employer. Therefore, requests to add: "It is further agreed that the Contractor shall be responsible for statutory approvals necessary for engagement of his workmen at site. However, all other government/statutory approvals in relation to the project shall be obtained by Employer and in the event of any delays in the same, shall entitle the Contractor for equitable extension of time and adjustment in Contract Price." | Contractual | All necessary approvals required for initiation of Construction activity at site are in place. However, any approval/permit if required during the execution stage shall be under the scope of Contractor. SECI and State government will provide assistance to the Contractor in obtaining all such approvals.
178 | IV - GENERAL CONDITIONS OF CONTRACT (GCC) | 127 / 264 | 43.1.2 | 43.1.2. - If, for reasons attributable to the Contractor, the guaranteed level of the Functional Guarantees specified under Technical Specifications are not met either in whole or in part, the Contractor shall, within a mutually agreed time, at its cost and expense make such changes, modifications and/ or additions to the Plant or any part thereof as may be necessary to meet such Guarantees. The Contractor shall notify the EMPLOYER/Owner upon completion of the necessary changes, modifications and/or additions, and shall seek the EMPLOYER’s/Owner’s consent to repeat the Guarantee Test. If the level of the specified Functional Guarantee parameters, as demonstrated even during repeat of the Guarantee Test(s), are outside the acceptable shortfall limit, the EMPLOYER//Owner may at its option, | Bidder request to define what is the acceptable shortfall limit. Please specify the value clearly for the acceptable shortfall limit.\ | Contractual | Kindly refer to the Amendment related to LD under the Technical Specification document.
179 | IV - GENERAL CONDITIONS OF CONTRACT (GCC) | 127 / 264 | 43.1.2 | 43.1.2. - If, for reasons attributable to the Contractor, the guaranteed level of the Functional Guarantees specified under Technical Specifications are not met either in whole or in part, the Contractor shall, within a mutually agreed time, at its cost and expense make such changes, modifications and/ or additions to the Plant or any part thereof as may be necessary to meet such Guarantees. The Contractor shall notify the EMPLOYER/Owner upon completion of the necessary changes, modifications and/or additions, and shall seek the EMPLOYER’s/Owner’s consent to repeat the Guarantee Test. If the level of the specified Functional Guarantee parameters, as demonstrated even during repeat of the Guarantee Test(s), are outside the acceptable shortfall limit, the EMPLOYER//Owner may at its option, either • Reject the Equipment and advise immediate replacement to suit the provisions of Technical Specification without any additional cost or; • Reject the Equipment and recover the payments already made, or; • Terminate the Contract and recover the payments already made, or; • Accept the equipment after levy of liquidated damages in accordance with the provisions specified. | Bidder request to modify the clause as follows, 43.1.2. - If, for reasons attributable to the Contractor, the guaranteed level of the Functional Guarantees specified under Technical Specifications are not met either in whole or in part, the Contractor shall, within a mutually agreed time, at its cost and expense make such changes, modifications and/ or additions to the Plant or any part thereof as may be necessary to meet such Guarantees. The Contractor shall notify the EMPLOYER/Owner upon completion of the necessary changes, modifications and/or additions, and shall seek the EMPLOYER’s/Owner’s consent to repeat the Guarantee Test. If the level of the specified Functional Guarantee parameters, as demonstrated even during repeat of the Guarantee Test(s), are outside the acceptable shortfall limit, the EMPLOYER//Owner may at its option, either • Reject the Equipment and advise immediate replacement to suit the provisions of Technical Specification without any additional cost or; • Reject the Equipment and recover the payments already made, or; • Terminate the Contract and recover the payments already made, or; • Accept the equipment after levy of liquidated damages in accordance with the provisions specified. "as the sole remedy, may take over the equipment upon levy of liquidated damages subjected to a maximum of 5% of the contract price for failure to meet functional guarantees. | Contractual | The terms and conditions of the tender document shall prevail.
180 | IV - GENERAL CONDITIONS OF CONTRACT (GCC) | 126 / 264 | 38.2 | 38.2 No adjustment in Contract Price shall be allowed for reasons of such delays and extensions granted except as provided in Tender Document, where the EMPLOYER/ Owner reserves the right to seek indulgence of Contractor to maintain the agreed Time Schedule of Completion. In such an event the Contractor shall be obliged for working by Contractor's personnel for additional time beyond stipulated working hours as also Sundays and Holidays and achieve the completion date/interim targets. | The Bidder requests for deletion of this clause. Any delays or disruptions caused due to events beyond the control of the Contractor, shall entitle the Contractor for both extension of time and cost compensation/adjustment in Contract Price. | Contractual | The terms and conditions of the tender document shall prevail.
181 | IV - GENERAL CONDITIONS OF CONTRACT (GCC) | 133 / 264 | 51.1 | However, these adjustments would be restricted to direct transactions between the Owner and Contractor and Bought out items (dispatched directly from sub vendor's works to Site). These adjustments shall not be applicable on procurement of raw materials, intermediary components and intermediary services etc. by the Contractor. | Bidder request that the "Statutory variations due to imposition of new taxes, duties and levies or increase/reduction/withdrawal of existing GST, duties and levies by the Central or State Government is applicable for the Raw materials too which can impact the price of the finished goods. Please clarify. | Contractual | As clearly stated, the adjustment due to change in law shall be restricted to direct transactions between the Owner and Contractor and Bought out items (dispatched directly from sub vendor's works to Site). These adjustments shall not be applicable on procurement of raw materials, intermediary components and intermediary services etc. by the Contractor.
182 | IV - GENERAL CONDITIONS OF CONTRACT (GCC) | 136 / 264 | 55.2 | 55.2 - Where approval/ review of drawings before manufacture/ construction/ fabrication has been specified, it shall be Contractor's responsibility to have these drawings prepared as per the TS and get it approved before proceeding with manufacture/ construction/ fabrication as the case may be. Any change that may have become necessary in these drawings during the execution of the work shall have to be carried out by the Contractor at no extra cost. All as built drawings shall bear the certification stamp duly signed by both the Contractor and Engineer-in-Charge/Project Manager. The Contractor shall incorporate any modifications and/ or corrections as highlighted/notified and submit the drawings for approval practically within the next 7 working days. | As there is no clear change order procedure in the contract. Bidder requests SECI to introduce a change order clause similar to FIDIC provisions. | Contractual | The terms and conditions of the tender document shall prevail.
183 | IV - GENERAL CONDITIONS OF CONTRACT (GCC) | 142 / 264 | 70 | 70.1 i) Subject to the provisions of sub-para (ii) of this clause, the Contractor shall, if ordered in writing by the Engineer-in-Charge/Project Manager, or his representative, temporarily suspend the Works or any part thereof for such written order, proceed with the Work therein ordered to be suspended until, he shall have received a written order to proceed therewith. The Contractor shall not be entitled to claim compensation for any loss or damage sustained by him by reason of temporary suspension of the Works aforesaid. However, suitable time extension may be considered at the sole discretion of the owner. ii) In case of suspensions of entire Work, ordered in writing by Engineer-in-Charge/Project Manager, for a period of more than 03 (Three) months, the Contractor shall have the option to terminate the Contract. | Bidder requests that the Contractor shall be entitled to both extension of time and costs compensation in the event such suspension is ordered not due to the breach of the contractor. | Contractual | The terms and conditions of the tender document shall prevail. However, all such cases will be dealt in line with the terms and conditions of the tender document.
184 | IV - GENERAL CONDITIONS OF CONTRACT (GCC) | 154 / 264 | 84.1 | 84.1 Should the Contractor consider that he is entitled to any extra payment for any extra/ additional Works or Material change in original Specifications carried out by him in respect of Work he shall forthwith give notice in writing to the Engineer-in-Charge/Project Manager that he claims extra payment. Such notice shall be given to the Engineer-in-Charge/Project Manager upon which Contractor bases such claims and such notice shall contain full particulars of the nature of such claim with full details of amount claimed. Irrespective of any provision in the Contract to the contrary, the Contractor must intimate his intention to lodge claim on the Owner within 10 (Ten) days of the commencement of happening of the event and quantify the claim within 30 (Thirty) days, failing which the Contractor will lose his right to claim any compensation /reimbursement/ damages etc. or refer the matter to arbitration. Separate bills shall be raised for the extra claim. | Bidder requests to remove " failing which the Contractor will lose his right to claim any compensation /reimbursement/ damages etc. or refer the matter to arbitration" All matters shall be subject to arbitration and the claims shall be subject to laws of Limitation only. no matter shall be considered as an "excluded matter' from being referred to arbitration. | Contractual | The terms and conditions of the tender document shall prevail.
185 | V - SPECIAL CONDITIONS OF CONTRACT (SCC) | 173 / 264 | 3.1 | Signing of Contract Agreement - Zero Date (D) | As the land is provided by the employer, bidder request that the Zero Date (D) can start from the date of 100% encumbrance free handover of the land to the contractor for the project works or the Signing of Contract Agreement, whichever is later. Please accept. | Contractual | The Zero Date will be the date of signing of Contract Agreement. SECI will handover the encumbrance free land handover to the Contractor before signing of Contract Agreement.
186 | V - SPECIAL CONDITIONS OF CONTRACT (SCC) | 174 / 264 | 4. Point no. 6 | It is specially emphasized that it shall be the responsibility of the Bidders to have themselves familiarized with the prevailing conditions and that no claim relating thereto for additional payment or adjustment of a Contract price will be acceptable after the submission of their Bid. | Bidder's understanding is that bidder will take all the necessary information and shall put full efforts to get themselves familiarized with the prevailing conditions of the site. But even though if any unforeseeable condition arises then the bidder shall be eligible for claims relating thereto for additional payment or adjustment of a Contract price. | Contractual | All such cases arising in future will be dealt on case to case basis.
187 | V - SPECIAL CONDITIONS OF CONTRACT (SCC) | 174 / 264 | 4. Point no. 6 | It is specially emphasized that it shall be the responsibility of the Bidders to have themselves familiarized with the prevailing conditions and that no claim relating thereto for additional payment or adjustment of a Contract price will be acceptable after the submission of their Bid. | As the land is given by employer and as the bidder is unaware of the underground utilities at the land area to be provided by the employer for the project, Bidder request the employer to consider that the bidder shall be eligible for claims relating thereto for additional payment or adjustment of a Contract price. | Contractual | All such cases arising in future will be dealt on case to case basis.
188 | V - SPECIAL CONDITIONS OF CONTRACT (SCC) | 174 / 264 | 4. Point no. 10 | Cutting of trees, bushes and vegetation from site (including permission from local authorities) and disposal thereof. The site should be maintained in vegetation free condition during erection stage (at any point of time) i.e., up to start of O&M Contract. | As the land is identified by the employer, bidder request the employer to consider the permission for tree cutting from the authorities in employer's scope. Bidder can consider the scope of tree cutting but the permission for the same from authorities to be sought by the employer. Please accept. | Contractual | As the land owner is SECI, SECI will provide the necessary approval for cutting of bushes and trees (if required).
189 | V - SPECIAL CONDITIONS OF CONTRACT (SCC) | 175 / 264 177 / 264 | 9 | The Contract Performance Security shall be in the form of Bank Guarantee only and shall be in the currency of the Contract and will be issued in the name of the Owner as “Solar Energy Corporation of India Ltd”. PBG will also be acceptable in the form of Surety Bond from an Insurer as per the guidelines issued by the Insurance Regulatory and Development Authority of India (IRDAI) strictly as per the Format – 32. | Both the clauses are contradictory. Bidder's understanding is that Insurance Surety bond can be submitted for Contract performance security. Please clarify. | Contractual | Yes, PBG is accepted in form of Surety Bond.
190 | V - SPECIAL CONDITIONS OF CONTRACT (SCC) | 176 / 264 | 9. Point no. 1 | First Stage (Supply and Services): The value of the Contract Performance Security shall be 5% (Five percent) of the Contract Value (i.e., total sum of the Supply & Service Contract). This Performance security will be valid for a total period of 75 Months (12 Months Project commissioning period) + prescribed O & M Period, i.e., 60 Months + 03 Months additional) from the date of its issuance. The successful bidder can submit Contract Performance Security with initial validity of 36 months and the same may be extended after every 36 months till completion of the total 75 months period. | Bidder request to consider the first stage of Contract performance security of 5% of the contract value validity upto the DLP of the contract and introduce the second stage of performance security for the O&M period separately with a value of 5% of O&M contract value with validity till the end of O&M period. | Contractual | The terms and conditions of the tender document shall prevail.
191 | V - SPECIAL CONDITIONS OF CONTRACT (SCC) | 177 / 264 | 10 | In the matter of connectivity of Plant to DISCOM’s substation, the Owner will take the necessary connectivity permission, however, all the other permissions and clearances as deemed required by the State Agency/DISCOM for Bay allocation, technical/regulatory compliance for interconnection, ROW etc. are to be taken by the Contractor. All the required fees including statutory fees, Supervision charges etc. shall be paid / born by the contractor. | As the connectivity is sought by employer, bidder request the employer to consider all the other permissions and clearances as deemed required by the State Agency/DISCOM for Bay allocation, technical/regulatory compliance for interconnection, ROW etc. under employer's scope. Also, the required fees including statutory fees, Supervision charges etc. shall be paid / born by the employer. Please accept. | Contractual | The terms and conditions of the tender document shall prevail.
192 | V - SPECIAL CONDITIONS OF CONTRACT (SCC) | 178 / 264 | 12 point no. v | It shall be duty of the Contractor to inspect the materials supplied to him at the time of taking delivery/handing over and satisfy himself that they are in good condition. After the materials have been delivered by the Owner, it shall be the responsibility of the Contractor to keep them in good condition and if the materials are damaged or lost, at any time, they shall be repaired and/ or replaced by him at his own cost. Upon identifying a damaged module post handing over of the Modules to the contractor, the contractor shall keep them in a separate storage and enlist them, upon verification, the entire damaged modules shall be replaced. In case of any discrepancy, the differential modules cost shall be debited from contractors' RA bills. | Any modules damages inside the module boxes will not be visible or able to identify by the contractor during the unloading of the modules. So, clear procedure for the reporting of any module damage during unboxing the modules to be formulated at site and the replacement of those damaged modules to be taken care by the employer. Please clarify. | Contractual | The Module supplier will arrange for replacement of defective modules for the period of 04 months from the date of delivery of such module pallets at site, in case such module pallets is not opened at the time of delivery and the visual inspection of such pallets is carried out at a later stage by the EPC Contractor.
193 | V - SPECIAL CONDITIONS OF CONTRACT (SCC) | 178 / 264 | 12 point no. vi | The Owner shall not be liable for delay in supply or non-supply of any materials which the Owner has undertaken to supply where such failure or delay is due to natural calamities, act of enemies, transport and procurement difficulties and any circumstances beyond the control of the Owner. In no case, the Contractor shall be entitled to claim any compensation or loss suffered by him on this account. | Bidder request to modify the clause as follows, The Owner shall not be liable for delay in supply or non-supply of any materials which the Owner has undertaken to supply where such failure or delay is due to natural calamities, act of enemies, transport and procurement difficulties and any circumstances beyond the control of the Owner. The Contractor shall be entitled to claim reasonable compensation or loss suffered by him on this account which can be verified and approved by the Project Manager/EIC. | Contractual | The terms and conditions of the tender document shall prevail.
194 | V - SPECIAL CONDITIONS OF CONTRACT (SCC) | 180 / 264 | 15 | Schedule of Rates & Payments: 10% interest free advance 70% on pro rata basis against supply, receipt and acceptance of Materials at site 10% against successful erection, testing and commissioning of materials on pro rata basis at site. 10% against submission of the BG of the equivalent amount & against the Operational Acceptance of the plant Facility pursuant to successful Guarantee Tests and demonstration of Performance Ratio (PR) including submission of all as-built drawings and O&M manual. | As the given payment terms leads to negative cashflow to the bidder, to prepare a more competitive bid bidder request to modify the payment terms as follows as per the standard industry practise, 15% interest free advance 55% against dispatch of Material from Manufacturer’s work 20% on pro rata basis against supply, receipt and acceptance of Materials at site 7.5% against successful erection, testing and commissioning of materials on pro rata basis at site. 2.5% against submission of the BG of the equivalent amount & against the Operational Acceptance of the plant Facility pursuant to successful Guarantee Tests and demonstration of Performance Ratio (PR) including submission of all as-built drawings and O&M manual. | Contractual | The terms and conditions of the tender document shall prevail.
195 | V - SPECIAL CONDITIONS OF CONTRACT (SCC) | 181 / 264 | 15. B | For Erection, Testing and Commissioning Portion, the payment shall be made as detailed below: - 80% on pro-rata basis on completion of installation of equipment on certification by the Engineer-In-Charge/ Project Manager 10% against successful commissioning 10% against submission of the BG of the equivalent amount & against the Operational Acceptance of the plant Facility pursuant to successful Guarantee Tests and demonstration of Performance Ratio (PR) including submission of all as-built drawings and O&M manual. | As the given payment terms leads to negative cashflow to the bidder, to prepare a more competitive bid bidder request to modify the payment terms as follows as per the standard industry practise, 90% on pro-rata basis on completion of installation of equipment on certification by the Engineer-In-Charge/ Project Manager 7.5% against successful commissioning 2.5% against submission of the BG of the equivalent amount & against the Operational Acceptance of the plant Facility pursuant to successful Guarantee Tests and demonstration of Performance Ratio (PR) including submission of all as-built drawings and O&M manual. | Contractual | The terms and conditions of the tender document shall prevail.
196 | V - SPECIAL CONDITIONS OF CONTRACT (SCC) | 181 / 264 | 15. B | For Civil & Allied works portion, of the First contract, the payment shall be made as detailed below: - 80% on pro-rata basis on completion of installation of equipment on certification by the Engineer-In-Charge/ Project Manager 10% against successful commissioning 10% against submission of the BG of the equivalent amount & against the Operational Acceptance of the plant Facility pursuant to successful Guarantee Tests and demonstration of Performance Ratio (PR) including submission of all as-built drawings and O&M manual. | As the given payment terms leads to negative cashflow to the bidder, to prepare a more competitive bid bidder request to modify the payment terms as follows as per the standard industry practise, 90% on pro-rata basis on completion of installation of equipment on certification by the Engineer-In-Charge/ Project Manager 7.5% against successful commissioning 2.5% against submission of the BG of the equivalent amount & against the Operational Acceptance of the plant Facility pursuant to successful Guarantee Tests and demonstration of Performance Ratio (PR) including submission of all as-built drawings and O&M manual. | Contractual | The terms and conditions of the tender document shall prevail.
197 | Form F-12 | 205 / 264 |  | Reference: Ministry of New & Renewable Energy (MNRE) Order No 283/22/2019-GRID SOLAR dated 23rd Sep 2020 & any amendments thereof, for the Public Procurement (Preference to Make in India) to provide for Purchase Preference (linked with local content) in respect of Renewable Energy (RE) Sector. | With reference to the clause, bidder understand that to meet 50% of local content for inverters, there are only few OEMs satisfying the local content requirement leading to Monopoly condition which will lead to cost and time impact. Considering the challenging execution timeline, we request you to waive the clause and allow us to use Inverters without local content. Also, bidder request to follow the following notification for the tender as per the standard industry practise which allows inverters to be sourced without local content, | Contractual | This being the CPSU Scheme tender, bidder must abide the Public Procurement Policy for Inverter.
198 | SECTION - VII SUB-SECTION A SCOPE OF WORKS | 6 / 316 | 1 Project Particulars | Supply of PV Modules: Supply of PV Modules at the Project Site shall be in the Scope of the Owner. The Owner shall deliver PV Modules at the Project site. However, for the purpose of bidding contractor may consider 540Wp Mono PERC module of 20.9% efficiency with dimensions 2278mm x 1134mm. | Bidder request to provide spare modules of 0.2% of the total quantity. | Contractual | The terms and conditions of the tender document shall prevail.
199 | SECTION - VII SUB-SECTION A SCOPE OF WORKS | 6 / 316 | 1 Project Particulars | Supply of PV Modules: Supply of PV Modules at the Project Site shall be in the Scope of the Owner. The Owner shall deliver PV Modules at the Project site. However, for the purpose of bidding contractor may consider 540Wp Mono PERC module of 20.9% efficiency with dimensions 2278mm x 1134mm. | As various factors like temperature coefficient and the IAM global factor etc., varies from one manufacturer to other manufacturer for even the same 540 Wp modules from different manufacturers, bidder request to share the .pan file for the modules to be supplied by the employer for the project or a reference .pan file based on which the tender PR commitment can be calculated. | Technical - Electrical | PAN File of the module supplied by the owner shall be provided to the successful bidder. However for Bidding Purpose Bidder may consider 540Wp Mono PERC module. For other technical details, please refer to Sl. No. 16 Amendment-1 SA - B: Project Specific Technical Details
200 | SECTION - VII SUB-SECTION A SCOPE OF WORKS | 6 / 316 | 1 Project Particulars | Location: Gadhi, Tehsil: Badnawar Nawapada, Rajod, Tehsil: Sardarpur | All the workings and offer will be prepared on the basis of the land parcel and boundary to be shared by SECI. As the land is provided by SECI, bidder understands that if any change in the land location or the change in boundary after the bid submission happens, then the cost impact due to the changes will be compensated as variation by the employer. Please clarify. | Contractual | The terms and conditions of the tender document shall prevail.
201 | SECTION - VII SUB-SECTION A SCOPE OF WORKS | 6 / 316 | 1 Project Particulars | Location: Gadhi, Tehsil: Badnawar Nawapada, Rajod, Tehsil: Sardarpur | As the land is given by the employer, bidder understands that the development of any kind of road access and access ROW till the site boundary is under the scope of the employer. Please clarify. | Contractual | All the scope related to access road till the site and ROW is under the scope of Contractor.
202 | SECTION - VII SUB-SECTION A SCOPE OF WORKS | 8 / 316 | 3.2 | The data for the PV modules (drawings, GTP and PAN files) to be procured by the Owner shall be provided to the Contractor for this estimation. | Bidder request to provide the data for the PV modules (drawings, GTP and PAN files) to be procured by the Owner | Technical - Electrical | PAN File of the module supplied by the owner shall be provided to the successful bidder. However for Bidding Purpose Bidder may consider 540Wp Mono PERC module. For other technical details, please refer to Sl. No. 16 Amendment-1 SA - B: Project Specific Technical Details
203 | SECTION - VII SUB-SECTION A SCOPE OF WORKS | 11 / 316 | 4.1 | Supply of Solar PV Modules is not in the scope of the EPC Contractor. It shall be the responsibility of the Owner to supply PV Modules at Project site, between 6 (six) to 11 (eleven) months from date of award of the Contract. | Bidder request to modify the clause as follows, Supply of Solar PV Modules is not in the scope of the EPC Contractor. It shall be the responsibility of the Owner to supply PV Modules at Project site, at equal tranches between 6 (six) to 11 (eleven) months from date of award of the Contract. | Contractual | The staggered delivery window will be finalized on the basis of mutually consultation between the BoS Contractor and SECI post award.
204 | SECTION - VII SUB-SECTION A SCOPE OF WORKS | 12 / 316 | 4.13 | 33 kV Over Head Transmission Line / Under Ground Cable including Poles / Towers, Conductors, Insulators, Cable Termination Kits and associated accessories from 33 kV Switchgear of inverter stations to 33/220 kV Pooling Substation including Right of Way, permits and approvals. | If the said 33 kV Over Head Transmission Line / Under Ground Cable including Poles / Towers, Conductors, Insulators, Cable Termination Kits and associated accessories from 33 kV Switchgear of inverter stations to 33/220 kV Pooling Substation goes beyond the project boundary, then the Right of Way, permits and approvals for the same should be under the scope of employer. Please clarify | Technical - Electrical | It shall be under the scope of Contractor. Terms and conditions of the tender document shall prevail.
205 | SECTION - VII SUB-SECTION A SCOPE OF WORKS | 12 / 316 | 4..17 | 220 kV Over Head Transmission Line / Under Ground Cable (suitable for evacuation of 200 MVA) including Towers, Conductors, OPGW cable, Insulators, Cable Termination Kits and associated accessories from 33/220 kV Pooling Substation to Interconnecting Substation as per CTU drawings/specifications including Right of Way, permits and approvals, CTU supervision and maintenance charges. | As the site location and land is identified by the employer, bidder request to consider the 220 kV TL Right of Way (ROW) under employer's scope. | Technical - Electrical | It shall be under the scope of Contractor. Terms and conditions of the tender document shall prevail.
206 | SECTION - VII SUB-SECTION A SCOPE OF WORKS | 15 / 316 | 5.16 | Installation, Testing and Commissioning of 220 kV Over Head Transmission Line / Underground Cable from 33/220 kV Solar Park Substation to Interconnecting Substation as per CTU drawings/specifications including Right of Way, permits and approvals, CTU supervision and maintenance charges. | As the site location and land is identified by the employer, bidder request to consider the 220 kV TL Right of Way (ROW) under employer's scope. | Technical - Electrical | It shall be under the scope of Contractor. Terms and conditions of the tender document shall prevail.
207 | SECTION - VII SUB-SECTION A SCOPE OF WORKS | 15 / 316 | 5.16 | Installation, Testing and Commissioning of 220 kV Over Head Transmission Line / Underground Cable from 33/220 kV Solar Park Substation to Interconnecting Substation as per CTU drawings/specifications including Right of Way, permits and approvals, CTU supervision and maintenance charges. | Bidder request to provide the proposed TL route from SECI or the route survey report done by the employer to follow the same. | Technical - Electrical | The route survey has not been carried out by the Employer and shall be under the scope of the Contractor. The terms and conditions of the tender document shall prevail.
208 | SECTION - VII SUB-SECTION A SCOPE OF WORKS | 17 / 316 | 6.4 | Installation, Testing and Commissioning of 220 kV Over Head Transmission Line / Underground Cable from 33/220 kV Solar Park Substation to Interconnecting Substation as per CTU drawings/specifications including Right of Way, permits and approvals, CTU supervision and maintenance charges. | Cutting of trees shall be taken under the scope of bidder, but bidder request employer to consider the necessary permissions and approvals for tree cutting under employer's scope | Technical - Electrical | It shall be under the scope of Contractor. Terms and conditions of the tender document shall prevail.
209 | SECTION - VII SUB-SECTION A SCOPE OF WORKS | 18 / 316 | 7.1 | Obtaining statutory approvals /clearances/ compliances on behalf of the Employer from various Government Departments, not limited to, the following: • Pollution control board clearance, if required • Mining Department, if required • Forest Department, if required • All other approval as and when, as necessary for setting up of the solar power plant including CEIG/ CEA, power evacuation, etc. as per the suggested guidelines. | As Employer is the project owner, bidder request the employer to consider all the project related approvals as m mentioned under employer's scope. However, bidder can consider CEIG clearance for bidder's scope of work under bidder's scope. | Technical - Electrical | The terms and conditions of the tender document shall prevail.
210 | SECTION - VII SUB-SECTION D GENERAL ANNEXURE J Functional Guarantee (FG) Test Procedure | 258 / 316 | 2.1 | A Performance Ratio test shall be carried out after the commissioning of Plant Facilities to demonstrate that the plant has achieved the Guaranteed Performance Ratio in line with requirements under section VII of the bidding document. This will be one of the pre-conditions for the Plant Operational Acceptance. Performance Ratio (PR) test period would be continuous measurement of 30 consecutive days. | Bidder request to add a clause as follows, If the commencement of PR test gets delayed more than 3 months due to reasons not attributable to the contractor, the payments related to the operational acceptance shall be released against submission of equivalent Bank Guarantee. | Technical - Electrical | The criteria for Operational Acceptance and the O&M period have been updated. Please refer to Sl. No. 21, 24, and 25 of Amendment-1. However, no such clause as requested by the bidder shall be added.
211 | SECTION - VII SUB-SECTION D GENERAL ANNEXURE J Functional Guarantee (FG) Test Procedure | 261 / 316 | 2.1.4.3 | If the If the EPC Contractor is not able to demonstrate guaranteed PR during this period, two more chances shall be given to demonstrate the same after incorporation of suitable corrective measures. In case the contractor fails to achieve guaranteed PR even after the two more chances, further action shall be taken as per the provisions of contract. | Bidder's understanding is that as like target generation test provision of the tender for PR demonstration also If the contractor claims that the shortfall is due to non-performance of the PV Modules, necessary evidence clearly showing that the shortfall in PR is due to PV module and not attributable to the systems supplied by bidder, erection issues and/or O&M practices followed by the bidder during PR Test, should be provided to the Employer. Please clarify. | Technical - Electrical | The criteria for Operational Acceptance and the O&M period have been updated. Please refer to Sl. No. 16, 21, 24, and 25 of Amendment-1. However, any shortfall in generation during OTGT and during O&M Period resulting from the non-performance of the PV Modules (Defective Modules) shall be intimated by the BoS Bidder to the Owner at the earliest. The responsibility for measuring the PV module performance output by using necessary equipment, shall lie with the BoS Contractor.
212 | SECTION - VII SUB-SECTION D GENERAL ANNEXURE J Functional Guarantee (FG) Test Procedure | 264 / 316 | 3.2 | FOR SHORTFALL IN TARGET GENERATION – Liquidated damages of amount equal to the NPV of the estimated shortfall in cash flow resulting over the period of 25 years due to shortfall in actual generation against target generation, calculated at a tariff of Rs. 2.57 per unit (kWh) and discount rate of 6.8% shall be levied. | Bidder request to remove the mentioned LD as it is duplicating with the LD for shortfall in PR. | Technical - Electrical | Liquidated Damages clause for Operational Acceptance and During O&M period have been updated. Please refer to Sl. No. 22, 24 & 25 of Amendment-1.
213 | SECTION - VII SUB-SECTION F OPERATION & MAINTENANCE AGREEMENT Annexure 2 - Functional Guarantee | 310 / 316 | 1.E | In case the Project fails to generate any power continuously for 1 month any time during the O&M period, apart from the force majeure and grid outages as certified by competent authority from STU/ CTU, it shall be considered as “an event of default”. In the case of default the entire Contract Performance Security will be forfeited. | Bidder will take atmost care to maintain the functionality of the plant. However, bidder request to modify the clause as follows, In case the Project fails to generate any power continuously for 3 months any time during the O&M period, apart from the force majeure and grid outages as certified by competent authority from STU/ CTU, it shall be considered as “an event of default”. In the case of default the entire Contract Performance Security will be forfeited. | Technical - Electrical | The terms and conditions of the tender document shall prevail.
214 | SECTION - VII SUB-SECTION F OPERATION & MAINTENANCE AGREEMENT Annexure 2 - Functional Guarantee | 314 / 316 | Scheduling and Forecasting | The Contractor shall be responsible for appointing a Qualified Coordinating Agency if required by concerned authorities at the Pooling Substation Level for scheduling and forecasting activity. Also, the contractor shall be responsible for carrying out the forecasting and scheduling of the energy generation from the plant facility (In accordance with the Deviation Settlement Mechanism Regulations, as applicable). Scheduling given by the Contractors is such that no penalty is levied on the Employer due to any deviation of actual generation from scheduling beyond the allowed limit. If any penalty arises due to DSM after adjusting the payable and receivable imposed on the Employer due to such deviations beyond allowed limit, the same has to be paid by the contractor separately. If the contractor fails to pay such penalty, then it shall be recovered from the contractor's payment to be done by Employer. | Though the Bidder shall follow the best industry practice for Scheduling and Forecasting, but still as the Solar Power generation vastly depends on the weather, which is beyond the control of the Bidder. Hence, the Bidder requests to share the penalty equally between the Bidder and the Employer in case of such penalty imposed by the competent authority. | Technical - Electrical | The terms and conditions of the tender document shall prevail.
215 | General |  |  |  | Bidder request to provide the .kmz file of the land, geotechnical investigation of the land and the hydrology report for the land | Technical - Civil | Topographical Survey Report has been shared for reference. Other reports are not available.
216 | General |  |  |  | Bidder request to indicate the preferred location for Plant end substation 220kV in the layout | Technical - Electrical | To be determined during detailed engineering.
217 | SECTION - VII SUB-SECTION A SCOPE OF WORKS | 7 / 316 | 1 Project Particulars | Performance Ratio (at 220 kV side of Plant Pooling Substation) For Operational Acceptance: 81.1% | As it is a BoS tender, supply of modules is with Employer, but there is no specific data about the make and model or .pan file of the module to be supplied by the employer. Please be informed that .pan file is very crucial for our internal calculation for the PR commitment. In view of the above, we put forward the following requests, Please share the .pan file of the module to be supplied for the execution of the subject tender or a reference .pan file which can be used for the tender PR commitment. Also, we request you to introduce a clause for PR correction based on the difference in technical parameters between the reference and actual .pan file of the project provided reference .pan file is given at tendering stage. (Or) We propose “O&M TARGET GENERATION TEST (OTGT)” (procedure attached for your reference as Annexure - 1) which is followed in case of BoS tenders by other PSUs. We request you to consider the proposed procedure and to incorporate the same. | Technical - Electrical | 1. PAN File of the module supplied by the owner shall be provided to the successful bidder. However for Bidding Purpose Bidder may consider 540Wp Mono PERC module. For other technical details, please refer to Sl. No. 16 Amendment-1 SA - B: Project Specific Technical Details 2. The criteria for Operational Acceptance and the O&M period have been updated. Please refer to Sl. No. 21, 24, and 25 of Amendment-1.
218 | General - Site visit |  |  |  | During the site visit we are not able to identify if any part of the land comes under forest department. Bidder request to clarify the same. | Contractual | Land is not under forest department.
219 | General |  |  |  | Bidder request to intimate the land handover timelines to the contractor. Bidder's understanding is that 100% encumbrance land required for the project will be handed over to the bidder at the time of NOA. Please clarify. | Contractual | 100% encumbrance free land will be provided to the Contractor before the Zero Date of signing of Contract Agreement.
220 | General |  |  |  | As the project location and land is identified by the employer, bidder request to consider any kind of project land related ROW to be taken care by employer. Bidder request to add a clause as follows, “Employer will give full possession of and accord all rights of unencumbered access to the project land and associated Land for Sub-station. In case of hindrance due to local issues, same has to be communicated to the employer immediately. However in case if the overall Project timelines are delayed on account of such hindrances, which is well substantiated and validated based on factual evidences, then suitable time extension may be granted by SECI for all such reported hindrances. However, the contractor should endeavour to resolve all such site issues/hindrances first hand & in case of non resolution only, time extension case may be considered, for the cases as elaborated above” | Contractual | The terms and conditions of the tender document shall prevail.
221 | General |  |  |  | Bidder request to clarify the possession of the project land. Whether the entire project land is already in the possession of SECI? Please clarify. | Contractual | The complete land parcel in under SECI's name.
222 | General |  |  |  | Bidder request to clarify when the project land will be handed over to the bidder for commencement of project activities. | Contractual | Before the Zero Date.
223 | General |  |  |  | During site visit, it is observed that some houses are falling under the project area. Bidder understands that those houses will be cleared before the commencement of zero date and handover of the land to the bidder. Please clarify. | Contractual | 100% encumbrance free land will be provided to the Contractor before the Zero Date of signing of Contract Agreement.
224 |  |  |  |  | During site visit, several LT lines are observed passing through the project area. Bidder request to clarify the scope of LT lines shifting inside the project area. | Technical - Electrical | Shifting of LT lines that fall inside plant area shall be in the scope of the BoS Contractor. Tentative route of LT lines is provided in ‘Tentative Land Layout and Contour Details’.
225 |  |  | General | Access to site and ROW | Bidder request to clarify the following, "Kindly confirm that the Employer shall give full possession of and accord all rights of unencumbered access to the associated Land for project execution on or before the date of Effective Date also request Employer to take care of any local issues arrising out of the possession of and accord all rights of unencumbered access to the associated Land for project execution during the currency of the contract. In case of any delay in the grant of the site/ access to the contractor or delay in execution due to any local issues then due EOT and compensation for the additional cost would be granted by the employer." | Contractual | 100% encumbrance free land will be provided to the Contractor before the Zero Date of signing of Contract Agreement.
226 |  |  | General | Module Insurance and damage accountability | As it is a BoS tender and as the supply of modules are not under the scope of contractor clear clauses to be introduced for the module insurance and damage accountability. Bidder request the following as the module supply is under the scope of employer, module insurance should be under the scope of employer and joint inspection to be done during the module container opening and unloading at site by employer and the contractor and if any visual damage is found during the container opening the same to be taken care by the employer. Also, clear procedure for the reporting of any module damage during unboxing the modules to be formulated at site and the replacement of those damaged modules to be taken care by the employer. Please clarify. | Contractual | The clause regarding the Module warranty, Warranty insurance are suitably incorporate under the Module Supplier Scope. And further tri party visual inspection as mentioned in the tender will be carried out at the time of Unloading by SECI, Module Supplier and BoS Contractor. Further, the Module supplier will arrange for replacement of defective modules for the period of 04 months from the date of delivery of such module pallets at site, in case such module pallets is not opened at the time of delivery and the visual inspection of such pallets is carried out at a later stage by the EPC Contractor.
227 |  |  | PR Test procedure | Module degradation for the delay in PR Test | If the reason for delay in PR Test and the operational acceptance is not attributable to the contractor, then the corresponding module degradation for the time period of delay to be taken into account during the PR test and O&M guarantee to be conducted after the delay. | Technical - Electrical | The criteria for Operational Acceptance and the O&M period have been updated. Please refer to Sl. No. 21, 24, and 25 of Amendment-1.
228 |  |  | General | - | Bidder request for the addition of the below clause: If Employer fails or delays to release the payments and or perform any other obligations under this Agreement, The Contractor may, after giving not less than [21] days’ notice to Ex.Engineer, suspend work (or reduce the rate of work) unless and until the Contractor has received the Payment or the breach of Employer is remedied. The Contractor’s action shall not prejudice its other rights and entitlements including interest on delayed payments. If the Contractor suffers delay and/or incurs Cost as a result of suspending work (or reducing the rate of work), it shall be entitled to : (a) an extension of time for any such delay, if completion is or will be delayed, and (b) payment of any such Costs incurred as a result thereto. Termination Rights: The Contractor shall be entitled to terminate the Contract if: a) The breach of Employer is not remedied and/or continues despite suspension of contract by the Contractor b) Employer assigns, sublets or transfers this Contract in contravention to the terms of this Contract. c) Employer becomes bankrupt, insolvent, goes into liquidation (voluntary or otherwise), has a receiving or administration order made against him, compounds with his creditors, or carries on business under a receiver, trustee or manager for the benefit of his creditors, an order for corporate insolvency resolution process or liquidation is passed by a court/ tribunal, change of Control, or if any act is done or event occurs which (under applicable Laws) has a similar effect to any of these acts or events. ; Except in events under (c ) where the termination shall be immediate, the Contractor may upon giving 14 days’ notice to Employer, terminate this Contract in any of the other events listed out hereinabove, without prejudice to its other rights under contract or otherwise; The contractor shall be entitled to: i) return of all performance securities furnished by the Contractor under this Contract ii) payments which shall include: (a) the amounts payable for any work carried out for which a price is stated in the Contract; (b) the Cost of Plant and Materials ordered for the Works which have been delivered to the Contractor, or of which the Contractor is liable to accept delivery; (c) any other Cost or liability which in the circumstances was reasonably incurred by the Contractor in the expectation of completing | Contractual | The terms and conditions of the tender document shall prevail.
229 |  |  | 3.1 Issue of NOA/ LOA/ LOI (as applicable) | Zero Date (D) | Bidder request SECI to confirm the following, Bidder construes that the preconditions for Effective / Commencement Date shall be reckoned from the latest happening of all of the following activities (a) complete unhindered access to site shall be given to the Contractor, Construction Reference Drawings / all other documents for execution shall be provided by the Engineer to the Contract; (b) all project approvals shall be obtained by the Employer, (C ) Contractor should have submitted the Performance Securities as per the terms of the Agreement, (d) Within 30 days of LOA, the NTP and Advance Payments shall be also be released in terms of this Contract by the Employer. In the event of delay in Start Date or issuance of NTP and/or any of the aforesaid activities [except (C)], the Contractor shall be entitled to be compensated by both time and cost. In the event the delays are beyond 90 days, the Contractor shall have the option to terminate the Contract for Employer's default. | Contractual | Zero Date will be the date of signing of Contract Agreement.
230 |  |  |  | Contract Agreement format and execution | Bidder requests to provide the Contract Agreement format. Further, it is construed that the Contract Agreement will be signed in New Delhi and appropriate stamp duty applicable in New Delhi shall be borne by the Owner. Please clarify. | Contractual | The draft Contract Agreement will be shared with the successful bidder and same will be executed on Delhi's stamp paper.
231 | Section IV | 111 | GCC 19 | Force majeure | We seek for the inclusion of pandemics and epidemics in the definition of force majeure | Contractual | Pandemic is already considered under the Force Majeure clause. Kindly refer to the GCC section of the tender document.
232 | Section IV | 112 | GCC 20.2 | The Owner shall at its sole discretion upon reaching the maximum LD limit , as an alternative to the Liquidated Damages at its option, get work executed from elsewhere at the risk and cost of the Contractor irrespective of the fact whether the scope of Contract is identical to the original scope of Contract and in case the Owner chooses the alternative course as mentioned, it will be entitled to recover compensation/ damages from the Contractor irrespective of maximum limit prescribed under Clause 20.1. | We seek that the owner shall have the option of risk purchase only when the maximum limit of LD is reached. We further seek that once maximum limit of LD is reached, the owner may invoke the risk purchase clause and shall not entitled to levy further LD beyond the maximum limit. | Contractual | The terms and conditions of the tender document shall prevail.
233 | Section IV | 112 | GCC 20.3 | The Owner may by giving (01) one-month notice to the Contractor cancel the Contract without prejudice to the Owner’s right under Clauses 20.1 and 20.2 or any other provisions contained in the Contract to determine the Contract and claim damages from the Contractor | We seek that the owner shall be entitled to only levy LD and shall not be entitled to the right of cancelling the contract. | Contractual | The terms and conditions of the tender document shall prevail.
234 | Section IV |  | No specific clause | Termination by contractor | "The Contractor shall have a right to terminate the contract in the event the Employer fails to release certified payments or fails to certify the invoices of the Contractor for more than 45 days beyond the time provided in the Contract. Under such event of termination, the Contractor shall be entitled to release of all payments for the works performed until the effective date of termination, costs arising as a result of early determination including demobilisation costs, return of all securities furnished by the Contractor." | Contractual | The terms and conditions of the tender document shall prevail.
235 | Section IV | 115 | GCC 25.1 | Termination for owner's convenience | We seek that in the event of such termination, Contractor should also be entitled to reasonable loss of profits. | Contractual | The terms and conditions of the tender document shall prevail.
236 | Section IV |  | No specific clause | Suspension by contractor | We seek that If the Employer fails to make due payments or fulfil any other contractual obligations, the Contractor may suspend or reduce work after giving 21 days' notice, until the payment is made or the breach is remedied. This does not affect the Contractor’s other rights, including interest on delayed payments. If suspension or reduced work causes delay or cost, the Contractor is entitled to: a. extension of time; (b) reimbursement of the costs incurred | Contractual | The terms and conditions of the tender document shall prevail. However, all such cases will be dealt in line with the terms and conditions of the tender document.
237 | Section IV | 120 | GCC 30 vi) | Subject to poor performance and prolonged delay of the project on account of inefficient sub-letting of the project work, Owner may take a final decision to terminate the contract of the principal Contractor which will be binding and non-revertible and henceforth no plea in this regard shall be entertained. | We kindly seek deletion | Contractual | The terms and conditions of the tender document shall prevail.
238 | Section IV | 122 | GCC 32.1.2 r/w 32.1.4 | The Contractor shall acquire, on behalf of Owner, in the Owner’s name, all permits, approvals and/or licenses from all local, state or national government authorities or public service undertakings in the Country/State where the Site is located that are necessary for the setting up of the Plant & operation of Plant till its desired life as mentioned under the Contract, including, but not limited to, entry permits for all imported Owner’s/EMPLOYER’s Equipment (if any). | We seek a clear matrix on the approvals/permits/licenses to be acquired by Contractor. | Contractual | All approvals / permits required in relation to the tender shall be in the scope of the BoS Contractor.
239 | Section IV | 112 | GCC 19.8 | The Contractor will not be entitled to claim any compensation for Force Majeure conditions and shall take appropriate steps to insure its men and materials utilized by it under the Contract. | We seek that the contractor shall be entitled to payments for the work done before the occurrence of the force majeure event. | Contractual | The payments will made in accordance with the Payment Terms listed in the SCC section of the tender document and as per the achieved milestone.
240 | Section IV | 112 | GCC 19.6 | Time for Performance of the relative obligation suspended by the force majeure shall stand extended by the period for which such Force Majeure clause lasts. | We seek for due extension of time and costs in case of any damages | Contractual | All such cases will be dealt on case to case basis in line with the terms and conditions of the tender document.
241 | Section IV | 123 | GCC 33 | The Contractor shall have to execute the Work in such place and conditions where other agencies may also be engaged for other works such as site grading, filling, and levelling, electrical and mechanical engineering works, etc. No claim shall be entertained due to Work being executed in the above circumstances. The Contractor shall allow such agencies to use the facilities like roads, etc constructed by the Contractor in order that they are able to carry out their respective scope of works unhindered | We seek that the contractor shall be entitled to due extension of time and costs in case of any damages caused to the works of the contractor by such other agencies at site. | Contractual | All such cases will be dealt on case to case basis in line with the terms and conditions of the tender document.
242 | Section IV r/w Section V | 165 and 182 | GCC 100 r/w GCC 101 r/w SCC | Arbitration AND Jurisdiction | We seek that any dispute arising between the parties shall be settled by Arbitration under the Arbitration and Conciliation Act. Number of arbitrators shall be 3 and the venue of arbitration shall be Chennai. We further seek that the courts at Chennai shall have exclusive jurisdiction. | Contractual | The terms and conditions of the tender document shall prevail.
243 | Section IV | 126 | GCC 38.2 | No adjustment in Contract Price shall be allowed for reasons of such delays and extensions granted except as provided in Tender Document, where the EMPLOYER/ Owner reserves the right to seek indulgence of Contractor to maintain the agreed Time Schedule of Completion. In such an event the Contractor shall be obliged for working by Contractor's personnel for additional time beyond stipulated working hours as also Sundays and Holidays and achieve the completion date/interim targets | We seek for additional cost and due extension of time incase of delays due to reasons attributable to the employer | Contractual | All such cases will be dealt on case to case basis in line with the terms and conditions of the tender document.
244 | Section IV | 131 | 46.1 | Unless otherwise terminated under the provisions of any other relevant clause, this Contract shall be deemed to have been completed at the expiration of the Period of Liability/ Validity of the Contract as provided under Section - V, Special Conditions of Contract (SCC). | We seek clarity as expiration of period of validity is not provided in the SCC | Contractual | Bid Validity is of 180 days as mentioned in the BDS section of the tender document.
245 | Section IV | 133 | 50.2 | During monsoon and other period, it shall be the responsibility of the Contractor to keep the construction work site free from water logging at his own cost. | We seek that if there any damages due to monsoons, the contractor shall be entitled to due extension of time and costs | Contractual | All such case will be dealt on case to case basis in line with the terms and conditions of the tender document.
246 | Section IV | 134 | 52.1 | Overtime work is permitted in cases of need and the Owner will not compensate the same. Shift working at 2 or 3 shifts per day may become necessary and the Contractor should take this aspect into consideration for formulating his rates. No extra claims will be entertained by the Owner on this account. | We seek that the contractor shall be entitled to additional costs if the contractor works overtime due to extra works assigned by the owner. | Contractual | The terms and conditions of the tender document shall prevail.
247 | Section V | 178 | GCC 60 r/w SCC 12 vi) | The Owner shall not be liable for delay in supply or non-supply of any materials which the Owner has undertaken to supply where such failure or delay is due to natural calamities, act of enemies, transport and procurement difficulties and any circumstances beyond the control of the Owner. In no case, the Contractor shall be entitled to claim any compensation or loss suffered by him on this account. | We seek that the contractor shall be entitled to due extension of time. | Contractual | All such cases will be dealt on case to case basis and the Contractor will be passed the suitable extension if delay is on Owner part related to delay in supply of Modules.
248 | Section IV | 142 | GCC 69 | The decision of the Engineer-in-Charge/Project Manager as to any question arising under this clause shall be final and conclusive. No additional time for Project completion shall be granted for undertaking such replacement/ rectification works by Contractor. | We seek that the dispute if any shall be referred to arbitration and the decision of the engineer-in-charge shall not be final and conclusive. | Contractual | The terms and conditions of the tender document shall prevail.
249 | Section IV | 142 | GCC 70.1 | i) Subject to the provisions of sub-para (ii) of this clause, the Contractor shall, if ordered in writing by the Engineer-in-Charge/Project Manager, or his representative, temporarily suspend the Works or any part thereof for such written order, proceed with the Work therein ordered to be suspended until, he shall have received a written order to proceed therewith. The Contractor shall not be entitled to claim compensation for any loss or damage sustained by him by reason of temporary suspension of the Works aforesaid. However, suitable time extension may be considered at the sole discretion of the owner | During suspension period, the contractor shall be eligible for additional cost incurred. Hence we seek modification as follows: i) Subject to the provisions of sub-para (ii) of this clause, the Contractor shall, if ordered in writing by the Engineer-in-Charge/Project Manager, or his representative, temporarily suspend the Works or any part thereof for such written order, proceed with the Work therein ordered to be suspended until, he shall have received a written order to proceed therewith. The Contractor shall not be entitled to claim compensation for any loss or damage sustained by him by reason of temporary suspension of the Works aforesaid. However, suitable time extension may be considered. at the sole discretion of the owner | Contractual | The terms and conditions of the tender document shall prevail.
250 | Section IV | 143 | GCC 73.2 | The decisions of the Project Manager in this regard shall be final and binding. | we seek deletion of this clause as the decision of the owner shall not be final and binding. | Contractual | The terms and conditions of the tender document shall prevail.
251 | Section IV | 144 | GCC 73.11 | If the Facilities or any part thereof cannot be used by reason of such defect and/or making good of such defect, the Defect Liability Period of the Facilities or such part, as the case may be, shall be extended by a period equal to the period during which the Facilities or such part cannot be used by the Owner because of any of the aforesaid reasons. Upon correction of the defects in the Facilities or any part thereof by repair/replacement, such repair/replacement shall have the defect liability period of twelve (12) months from such replacement | we shall seek the deletion of the portion relevant to extension of DLP to the full period(i.e. 12 months) without any cap which might lead to unending liability even for minor defect. We shall seek that the DLP be extended only to such facilities that are become non-usable for such duration due to defects or making good of such defects. If the Facilities or any part thereof cannot be used by reason of such defect and/or making good of such defect, the Defect Liability Period of the Facilities or such part, as the case may be, shall be extended by a period equal to the period during which the Facilities or such part cannot be used by the Owner because of any of the aforesaid reasons. Upon correction of the defects in the Facilities or any part thereof by repair/replacement, such repair/replacement shall have the defect liability period of twelve (12) months from such replacement | Contractual | The terms and conditions of the tender document shall prevail.
252 | Section IV | 144 | GCC 73 | No clause - exception to the Defect liability period | We shall seek that the obligation to rectify the defect during defect liability period shall not be applied on the following circumstances: Normal wear and tear, Defects Due to Employer’s Actions or Other Contractors, Misuse or Lack of Maintenance by Employer and any modification by the employer or its other contractors to the facilities . | Contractual | The terms and conditions of the tender document shall prevail.
253 | Section IV | 146 | GCC 74 | From the commencement to completion of the Work & till the completion of O&M period (If applicable), the Contractor shall take full responsibility for the care for all works including all temporary works and in case any damages, loss or injury shall happen to the Work or to any part thereof or to any temporary works from any cause whatsoever, shall at his own cost repair and make good the same so that at completion the Work shall be in good order and in conformity in every respects with the requirement of the Contract and the Engineer-in- Charge's instructions. Also damage to external property of Third Parties | We seek modification so as to ensure that owner or any other contractor shall be responsible for any acts: From the commencement to completion of the Work & till the completion of O&M period (If applicable), the Contractor shall take full responsibility for the care for all works including all temporary works and in case any damages, loss or injury shall happen to the Work or to any part thereof or to any temporary works from any cause whatsoever except for the act of Owner or any other its contractor, shall at his own cost repair and make good the same so that at completion the Work shall be in good order and in conformity in every respects with the requirement of the Contract and the Engineer-in- Charge's instructions. Also damage to external property of Third Parties | Contractual | The terms and conditions of the tender document shall prevail.
254 | Section IV | 146 | GCC 74.1 | The decision taken by the Owner in this regard towards the amount to be recovered from the Contractor will be final and binding on the Contractor. | We seek that The decision of the owner shall not be final and binding. | Contractual | The terms and conditions of the tender document shall prevail.
255 | Section IV | 150 | GCC 78.1 | If any action is brought before a Court, Tribunal or any other Authority against the EMPLOYER/ Owner or an officer or agent of the EMPLOYER/ Owner, for the failure, omission or neglect on the part of the Contractor to perform any acts, matters, covenants or things under the Contract, or damage or injury or death caused by the alleged omission or negligence on the part of the Contractor, his agents, representatives or his Sub-Contractor's, or in connection with any claim based on lawful demands of Sub-Contractor's workmen suppliers or employees, the Contractor, shall in such cases indemnify and keep the EMPLOYER/ Owner and/ or their representatives harmless from all losses, damages, expenses or decrees arising out of such action. | We seek that this indemnity clause shall be applicable mutually. | Contractual | The terms and conditions of the tender document shall prevail.
256 | Section IV | 159 | GCC 94.12 | The EMPLOYER/ Owner shall not be liable for or in respect of any damages or compensation payable at law in respect or in consequence of any accident or injury to any workman or other person in the Employment of the Contractor or any Sub-Contractor and the Contractor shall indemnify and keep indemnified the EMPLOYER/ Owner against all such damages and compensation (save and except and aforesaid) and against all claims, demands, proceeding, costs, charges and expenses, whatsoever in respect or in relation thereto. | If the owner or its men or its other contractors is responsible for any loss/damage/injury caused to any person, then owner shall be responsible for the same. Therefore, we shall seek modification as follows: The EMPLOYER/ Owner shall not be liable for or in respect of any damages or compensation payable at law in respect or in consequence of any accident or injury to any workman or other person in the Employment of the Contractor or any Sub-Contractor, provided that if such injury or accident is caused due to owner or its means or its other contractors and the Contractor shall indemnify and keep indemnified the EMPLOYER/ Owner against all such damages and compensation (save and except and aforesaid) and against all claims, demands, proceeding, costs, charges and expenses, whatsoever in respect or in relation thereto. | Contractual | The terms and conditions of the tender document shall prevail.
257 | Section IV | 162 | GCC 98.1 | EMPLOYER/ Owner shall not be liable for or in respect of or arising out of any failure by the Contractor in the performance of his obligations under the Contract Document. The EMPLOYER/ Owner shall not be liable for or in respect of any demand or compensation payable by law in respect or in consequence of any accident or injury to any workmen or other person. In the employment of the Contractor or his Sub-Contractor the Contractor shall indemnify and keep indemnified the EMPLOYER/ Owner against all such damages and compensations and against all claims, damages, proceedings, costs, charges and expenses whatsoever in respect thereof or in relation thereto. | We seek modification as follows: EMPLOYER/ Owner shall not be liable for or in respect of or arising out of any failure by the Contractor in the performance of his obligations under the Contract Document. The EMPLOYER/ Owner shall not be liable for or in respect of any demand or compensation payable by law in respect or in consequence of any accident or injury to any workmen or other person caused due to any act of contractors or its men or its sub-contractors. In the employment of the Contractor or his Sub-Contractor the Contractor shall indemnify and keep indemnified the EMPLOYER/ Owner against all such damages and compensations and against all claims, damages, proceedings, costs, charges and expenses whatsoever in respect thereof or in relation thereto. | Contractual | The terms and conditions of the tender document shall prevail.
258 | Section IV | 163 | GCC 98.2 | Should the EMPLOYER/ Owner have to pay any money in respect of such claims or demands as aforesaid the amount so paid and the costs incurred by the EMPLOYER/ Owner shall be charged to and paid by the Contractor and the Contractor shall not be at liberty to dispute or question the right of the EMPLOYER/ Owner to make such payments notwithstanding the same, may have been made without the consent or authority or in law or otherwise to the contrary. | This clause imposes unconditional financial liability upon the contractor by way of allowing the owner to make payment even without legal requirement, authority or even without consent and also restricts the right to dispute the payment made by the contractor even for no fault of contractor. Hence we seek modification as follows: Should the EMPLOYER/ Owner have to pay any money in respect of such claims or demands as aforesaid the amount so paid and the costs incurred by the EMPLOYER/ Owner shall be charged to and paid by the Contractor and the provided that owner shall inform the same to the contractor in writing and opportunity shall be given to the contractor to determine the claim is arising out of act of contractor. Contractor shall not be at liberty to dispute or question the right of the EMPLOYER/ Owner to make such payments notwithstanding the same, may have been made without the consent or authority or in law or otherwise to the contrary. | Contractual | The terms and conditions of the tender document shall prevail.
259 | SECTION - VII SUB-SECTION A SCOPE OF WORKS | 6 of 316 | 1 | #VALUE! | 1. Kindly provide the .pan file along with the detailed specifications of the module. 2. Kindly specify the cable length associated with the module that should be considered. | Technical - Electrical | PAN File of the module supplied by the owner shall be provided to the successful bidder. However for Bidding Purpose Bidder may consider 540Wp Mono PERC module. For other technical details, please refer to Sl. No. 16 Amendment-1 SA - B: Project Specific Technical Details
260 | SECTION - VII SUB-SECTION A SCOPE OF WORKS | 6 of 316 | 1 | Module Mounting Structure Type - South Facing, Fixed Tilt | As this is a Balance of System (BOS) tender, the bidder requests the Details of the pitch and tilt angle specifications to be considered in the design. | Technical - Electrical | Please refer to Sl. No. 16 Amendment-1 SA - B: Project Specific Technical Details
261 | SECTION - VII SUB-SECTION A SCOPE OF WORKS | 6 of 316 | 1 | #VALUE! | 1. As the provided Annexure-A does not contain sufficient details, the bidder requests that the coordinates and .kmz file for the location be shared, clearly marking the boundaries, the 33kV and 220kV transmission line (TL) corridors, tower locations, solar park substation location, and any existing canals or roads. 2. Additionally, the bidder expects to be provided with plot-wise area details if the plant location is spread across different parcels. | Technical - Electrical | 1. 220 kV transmission line (OHTL/UG cable) with all accessories, ROW, permits/approvals, 220 kV bay at interconnecting substation (including equipment shifting/replacement), and CTU supervision & maintenance charges shall be in the scope of the Contractor. Kindly refer to Clause No. 4.17 and 4.18 of SS-A SOW of tender document. 2. Refer to Sl. No. 56 of Amendment-1. CAD file has been shared.
262 | SECTION - VII SUB-SECTION A SCOPE OF WORKS | 7 of 316 | 1 | #VALUE! | 1. As this is a Balance of System (BOS) tender, the bidder is unable to commit to the specified requirement and therefore requests the removal of this clause. 2. Alternatively, if the clause cannot be removed, the bidder requests that monthly Performance Ratio (PR) values be provided, as PR is expected to vary across different months. 3.Considering the use of 540 Wp Monofacial modules achieving a Performance Ratio (PR) of 81.1% is comparatively high. Therefore the bidder requests a reconsideration of the PR. | Technical - Electrical | The criteria for Operational Acceptance and the O&M period have been updated. Please refer to Sl. No. 21, 24, and 25 of Amendment-1.
263 | SUB-SECTION D GENERAL ANNEXURE J Functional Guarantee (FG) Test Procedure | 263 of 316 | 2.2.4 | #VALUE! | 1. The bidder requests the following meteorological data for the site: a. Global Horizontal Irradiance (GHI) b. Diffuse Horizontal Irradiance (DHI) c. Ambient Temperature d. Surface Albedo 2. Alternatively, please confirm whether the bidder should use the SolarGIS or Metronome databank for the plant performance analysis. | Technical - Electrical | Monthly GHI & Albedo values have been provided at SA-B: Project Specific Technical Details
264 | SECTION - VII SUB-SECTION A SCOPE OF WORKS | 12 of 316 | 4.15 | ABT meters with all necessary metering rated CTs and PTs at the plant take-off point as well as at the interconnecting substation as per CEA Metering Regulations 2006 as amended time to time and state metering code. | The bidder requests clarification on the designated metering point for the plant. | Technical - Electrical | Metering Point shall be ABT Meter at the 220 kV Badnawar Substation (the Point of Interconnection). Please refer to Sl. No. 32 of Amendment-1.
265 | SECTION - VII SUB-SECTION A SCOPE OF WORKS | 12 of 316 | 4.14 | 33 kV Over Head Transmission Line / Under Ground Cable including Poles / Towers, Conductors, Insulators, Cable Termination Kits and associated accessories from 33 kV Switchgear of inverter stations to 33/220 kV Pooling Substation including Right of Way, permits and approvals. | The bidder requests the transmission line (TL) lengths for both the 33 kV and 220 kV lines. Additionally, the bidder seeks detailed specifications of the conductors proposed for use in these transmission lines. | Technical - Electrical | Design of associated civil, structural, electrical & mechanical systems for Transmission Line shall be in the scope of contractor. Kindly refer to Clause No. 3.5 of SS-A: SOW.
266 | SECTION - VII SUB-SECTION A SCOPE OF WORKS | 12 of 316 | 4.16 | 220 kV Over Head Transmission Line / Under Ground Cable (suitable for evacuation of 200 MVA) including Towers, Conductors, OPGW cable, Insulators, Cable Termination Kits and associated accessories from 33/220 kV Pooling Substation to Interconnecting Substation as per CTU drawings/specifications including Right of Way, permits and approvals, CTU supervision and maintenance charges. |  | Technical - Electrical | Design of associated civil, structural, electrical & mechanical systems for Transmission Line shall be in the scope of contractor. Kindly refer to Clause No. 3.5 of SS-A: SOW.
267 | SECTION - VII SUB-SECTION A SCOPE OF WORKS | 18 of 316 | 6.21 | Construction of wet type module cleaning system. | 1. The bidder seeks clarification regarding the module cleaning system, specifically whether a wet or dry cleaning method should be used in conjunction with the robotic cleaning system. 2. Additionally, the bidder requests clarification on whether semi-automatic or fully automatic robots should be employed for module cleaning operations. | Technical - Electrical | Bidder shall select Manual / Semi-automatic / Robotic module cleaning system with either dry or wet cleaning method based on site conditions. However, the offered solution must ensure effective soiling removal, be compatible with the module mounting structure proposed by bidder, and meet O&M efficiency.
268 | SECTION - VII SUB-SECTION C TECHNICAL SPECIFICATIONS (TS)- CIVIL, MECHANICAL & PLUMBING WORKS | 152 of 316 | 35.2 | Dry Cleaning System |  | Technical - Electrical | Bidder shall select Manual / Semi-automatic / Robotic module cleaning system with either dry or wet cleaning method based on site conditions. However, the offered solution must ensure effective soiling removal, be compatible with the module mounting structure proposed by bidder, and meet O&M efficiency.
269 | SECTION - VII SUB-SECTION B TECHNICAL SPECIFICATIONS (TS) – ELECTRICAL SYSTEM | 28 of 316 | 2.5 | In case of central inverters, average voltage drop in the cables (from PV Modules to PCU) shall be limited to 1.5 % of the rated voltage. In case of string Inverters, average voltage drop (from PV module to string inverter) shall be limited to 0.5% of the rated voltage drop. The Contractor shall provide voltage drop calculations in excel sheet. | The bidder requests that the average voltage drop in the cables (from PV modules to the PCU) be reconsidered and limited to 2% of the rated voltage. | Technical - Electrical | The terms and conditions of the tender document shall prevail.
270 | SECTION - VII SUB-SECTION B TECHNICAL SPECIFICATIONS (TS) – ELECTRICAL SYSTEM | 31 of 316 | 3.4.4 | Type-I+II surge protective device (SPD) conforming to IEC 61643-31 shall be connected between positive/ negative bus and earth on the DC side. Type-II SPD conforming to IEC 61643-11 shall be provided on the AC side. | The bidder requests the acceptance of Type II SPD for the DC side, in accordance with industry standards. | Technical - Electrical | The terms and conditions of the tender document shall prevail.
271 | SECTION - VII SUB-SECTION B TECHNICAL SPECIFICATIONS (TS) – ELECTRICAL SYSTEM | 34 of 316 | 3.7.1 | Active power regulation The PCU shall be able to limit the active power exported to the grid based on the set point provided through PCU front control panel. The PCU shall also be able to automatically the limit the active power after an increase in grid frequency above a pre-set value. The ramp rate shall be adjustable during operation and start-up after fault. The applicability of the requirement shall be as per CEA regulation and compliance. | Kindly provide the Grid-Limitation. | Technical - Electrical | Determination of Grid limitation, if any, is in the scope of the Bidder.
272 | SECTION - VII SUB-SECTION B TECHNICAL SPECIFICATIONS (TS) – ELECTRICAL SYSTEM | 34 of 316 | 3.7.2 | Reactive power control - The PCU shall be able to inject /absorb reactive power to/ from the grid based on the set point provided through PCU front control panel. The same shall be performed automatically with adjustable ramp rate based on dynamic changes in grid voltage or reactive power reference. | Bidder understands that the Reactive power compensation of the plant has been done with the help of Inverters. | Technical - Electrical | There is no restriction of technology to be adopted for reactive power compensation, Bidder may choose suitable technology. However, the Clause No. 3.7.2 specifies the PCU shall have the functionality of Reactive Power Compensation. Bidder shall ensure compliance with CEA (Technical Standards for Connectivity to the Grid) Regulations, 2007 and subsequent amendments, with regards to reactive power compensation at POI.
273 | SECTION - VII SUB-SECTION B TECHNICAL SPECIFICATIONS (TS) – ELECTRICAL SYSTEM | 63 of 316 | 12.2 | Protection level for the entire plant shall be Level-III. | Bidder request to consider lightning protection level for the entire plant to be level - 4 as per industry standards. | Technical - Electrical | The terms and conditions of the tender document shall prevail.
274 | SECTION - VII SUB-SECTION B TECHNICAL SPECIFICATIONS (TS) – ELECTRICAL SYSTEM | 63 of 316 | 12.4 | Necessary foundation/anchoring for holding the air terminal in position to be made after giving due consideration to shadow on PV array, maximum wind speed and maintenance requirement at site in future. | The bidder requests the removal of this clause, as the ESE lightning arrestor generates a moving shadow on the PV modules, which will have minimal impact on the plant’s generation. | Technical - Electrical | The terms and conditions of the tender document shall prevail.
275 | General | General | General | General | The bidder requests confirmation of the applicable corrosion Category for the project site. | Technical - Electrical | Corrosion category shall be considered as C3 as per the provisions of ISO 9223.
276 | General | General | General | General | Kindly provide the Single Line Diagram (SLD) of the plant for reference. | Technical - Electrical | Plant SLD is in the scope of bidder, to be finalised during detailed engineering.
277 | 4 Inverter Transformer and Auxiliary Transformer | Page No. 35 of 316 | 4.2 Technical Requirements | Inverter Duty Transformer (Winding material) | Winding material details for IDT is not mentioned in RFP. Bidder request to allow the Aluminium winding for IDT. Kindly confirm your acceptance for the same. | Technical - Electrical | Aluminium windings for IDT are acceptable subject to the transformer meeting technical specifications.
278 |  |  |  | Inverter Duty Transformer (Losses) | Losses details for IDT is not mentioned in RFP. Bidder request to accept the total losses (NL+FLL) upto 1.1%. Kindly confirm your acceptance for the same. | Technical - Electrical | Total IDT Losses have not been specified. The Contractor shall propose equipment losses during detailed engineering to meet the OTGT requirement at the Point of Metering.
279 |  |  |  | Inverter Duty Transformer (Insulating oil) | Insulating oil details for IDT is not mentioned in RFP. Bidder understand mineral oil can be used for IDTs. Kindly confirm your acceptance for the same. | Technical - Electrical | Insulating oil shall be as per IS 335/IEC 60296. Please refer Clause 4.1
280 |  |  |  | Tap Changer-OCTC, No. of steps shall be as per system requirement | Bidder understand OCTC +/-5% required on 2.5% steps. Please confirm the same. | Technical - Electrical | OCTC steps shall be determined during detailed engineering. Terms and conditions of the tender document shall prevail.
281 | 5 33 kV HT Switchgear Panel | Page No. 41 of 316 | 5.2 Technical Parameters | Internal Arc Classification - IAC-A, FLR system fault current for 1s | Bidder requests the internal arc type tested panel shall be applicable for indoor type panels only. This is not applicable for outdoor type panels placed in inverter Platform. | Technical - Electrical | The terms and conditions of the tender document shall prevail.
282 |  |  |  | Current Transformer Accuracy class - 0.2 for metering (0.2S for metering at outgoing feeder), 5P20 for protection | At ICR Level ICOG, CT Accuracy class will be 0.5 and at MCR HT Switchgear shall be 0.2 & 0.2s for metering (outgoing Feeder). Please confirm | Technical - Electrical | Terms and conditions of the tender document shall prevail. Kindly refer to Clause No. 5.2 (HT Switchgear) and Clause No. 8.2 (LT Switchgear)
283 |  |  |  | Voltage Transformer : 0.2 for metering, 3P for protection | At ICR Level ICOG, PT Accuracy class will be 0.5 and at MCR HT Switchgear shall be 0.2 & 0.2 for metering (outgoing Feeder). Please confirm | Technical - Electrical | Terms and conditions of the tender document shall prevail. Kindly refer to Clause No. 5.2 (HT Switchgear) and Clause No. 8.2 (LT Switchgear)
284 | 5.3 Switchgear Panel | Page No. 42 of 316 | 5.3.3 | The panel enclosure shall be constructed with CRCA steel/Aluzinc sheet. The thickness of load bearing members shall be minimum 3 mm and that of non-load bearing members shall be minimum 2 mm. | Switchgear Panel material & thickness will be as per OEM type tested design Only. | Technical - Electrical | Accepted. Please refer to Sl.No. 14 of Amendment-1
285 | 7 AC Cables | Page No. 50 of 316 | - | AC Cables | Details of cable conductor material type is not available in RFP. Bidder request to considered Aluminium cables for all type of cables. Kindly provide your acceptance. | Technical - Electrical | Accepted
286 | 8 Auxiliary Supply System | Page No. 51 of 316 | 8.3 | Auxiliary supply system | 1. Bidder understand 1 x 100% auxiliary transformer required at Main control room same shall be taped from 11 kV HT switchgear. 2. Auxiliary transformer requ. Is not specified for ICR room. bidder understand 1 x 100% auxiliary transformer required at inverter control room same shall be taped from LV side of IDT kindly provide your confirmation for the acceptance of the same. | Technical - Electrical | Accepted
287 |  |  |  | Auxiliary system of Pooling Substation shall incorporate redundant source of power supply for increased reliability. | Bidder will offer Common Auxiliary supply system for both Switchyard and CMCS. | Technical - Electrical | The terms and conditions of the tender document shall prevail.
288 |  |  | 8.4 | Following consideration shall be taken into account while sizing the auxiliary transformer: (i) 20% future load margin (ii) Total connected load at 0.8 power factor | Bidder understand 10 % margin is sufficient for auxiliary transformer at MCR & ICR both. Kindly provide your confirmation for both. | Technical - Electrical | The terms and conditions of the tender document shall prevail.
289 | 8 LT Switchgear | Page No. 52 of 316 | 9.3 | LT switchgear - Constructional Details | Bidder request to have consideration for Aluminium bus bar. Kindly confirm your acceptance for the same. | Technical - Electrical | Yes, aluminium bus bars shall be acceptable.
290 |  | Page No. 52 of 316 | 9.3.13 | Earth leakage relay with Core balance CTs (CBCT) shall be provided on main incoming feeders having phase CT ratio more than 50/1A. | Bidder propose MCCB with LSIG for earth fault protection instead of CBCT to provide the leakage protection in the LV panels. Please provide your acceptance for the same. | Technical - Electrical | The terms and conditions of the tender document shall prevail.
291 | 11 Earthing | Page No. 60 of 316 | 11.2.2. | The earth electrode shall be made of high tensile low carbon steel rod, molecularly bonded by high conductivity copper on outer surface with coating thickness not less than 250 micron as per relevant standards. | Bidder request to consider the mild steel rod for earthing Kindly confirm your acceptance for the same. | Technical - Electrical | The terms and conditions of the tender document shall prevail.
292 | 12 Lightning Protection System | Page No. 63 of 316 | 12.2 | Protection level for the entire plant shall be Level-III. | Bidder request to allow the Level-IV protection. | Technical - Electrical | The terms and conditions of the tender document shall prevail.
293 | 18.3 Relays | Page No. 78 of 316 | 18.3.15 | Each feeder shall have two lock out relays powered through two independent DC supplies. Each lock out relay shall send through two separate potential free output contacts signals to each of the two independent trip coils. | Bidder is proposing that each feeder will have only one Lock Out relay with one independent DC supply. | Technical - Electrical | The terms and conditions of the tender document shall prevail.
294 | 20 Illumination | Page No. 97 of 316 | 20.2.1 | This specification covers design, supply and installation of uniformly Illumination system along the peripheral corridor, access & internal roads, main control room & inverter rooms, switchyard and other facilities including entry points/gate(s) inside the plant area. | Bidder propose lighting pole shall be provided near to inverter station and periphery only, Internal road light is not required to avoid the shadow impact on the modules | Technical - Electrical | Please refer the table provided in Clause 20.3.1 for areas to be illuminated.
295 |  |  | 20.3.1 | Lighting Levels Internal / Access Roads - 4 Lux. | Bidder understand the average 4 lux to be maintained for peripheral roads. Please provide your acceptance for the same. | Technical - Electrical | Lighting level shall be designed with illuminance uniformity [Uo]of min 0.3. Please refer Clause 20.3.2.
296 | 20.3 Lighting Levels |  |  | Control Room and equipment rooms - 300 Lux Office - 300 Lux | Bidder proposes Lux level for SCADA and Admin rooms shall be avg 250 lux and rest rooms in MCR shall be 100 Lux. | Technical - Electrical | Lighting level shall be designed with illuminance uniformity [Uo]of min 0.3. Please refer Clause 20.3.2. Terms and conditions of the tender document shall prevail.
297 |  |  |  | General - Plant AC SLD. | Tender SLD is not available in RFP. Kindly share the same. | Technical - Electrical | Plant SLD is in the scope of the bidder. The same shall be finalised during detailed engineering.
298 |  |  |  | General - MCR Layout Plan | MCR layout plan is not available in RFP. Kindly provide the same with minimum requirement to be maintained for the MCR. | Technical -Civil | Refer Cl 16.2 (Page 31 of 58) under 'Sub-Section C: Technical Specifications (TS)- Civil, Mechanical & Plumbing Works' of Section VII. Terms and conditions of tender shall prevail
299 |  |  |  | General | Bidder understands that Radial scheme is allowed from the ICR to MCR feeder where two separate ICOG/HT panels (each 13.2MW max) capacity shall directly connected to single VCB vertical (26.4MW capacity) at MCR MV switchgear panel. | Technical - Electrical | Radial scheme is allowed. Equipment ratings & details shall be determined during detailed engineering.
300 |  |  |  | General | Kindly confirm the corrosion category to be considered for the equipment's. | Technical -Civil | Corrosion category shall be considered as C3 as per the provisions of ISO 9223.
301 |  |  |  | General - Short circuit withstand capability for cable. | Cable short circuit withstand will be sized as per Relay coordination study. Please confirm | Technical - Electrical | Accepted
302 |  |  |  | General | Kindly confirm the TRT value to be considered for the MV Cable sizing. | Technical - Electrical | Query not clear.
303 | 1 Project Particulars | Page No. 7 of 316 | - | Power Evacuation | Bidder understand that the Scope of work is limited upto the bay work of 400/220 kV S/S at badnawar, Dhar. Kindly provide your confirmation on same. | Technical - Electrical | Kindly refer to Clause No. 5.16 and Clause No. 5.17 of SS-A:SOW.
304 | Technical Specification-Section VII | 100 | 21.1.1 | Ingress protection -Pyranometer IP67 and Anemoter-IP66 | Bidder quotes that for Pyranometer and anemometer the ingress protection of IP65 is sufficient | Technical - Electrical | The terms and conditions of the tender document shall prevail.
305 | Technical Specification-Section VII | 101 | 22.1 | CCTV Cameras along with monitoring stations (sufficient numbers) and all other accessories required for its proper operation must be installed to have complete coverage of following areas for 24 hours. (ii) Along the Plant Perimeter: Covering complete perimeter of Plant Area to capture all possible intrusion | Bidder wishes to clarify that for solar power projects, CCTV at entire plant perimeter is not required . CCTV camera shall be considered only at strategic locations as specified in the RFP. Please confirm your acceptance for the same. | Technical - Electrical | Kindly refer to clause 22.1 (ii) Along the Plant Perimeter: Any strategic location in the Plant Area required to be monitored. The placement of cameras shall be determined accordingly during detailed engineering.
306 | Technical Specification-Section VII | 68 | 14.5.6 | The SCADA system shall have user-friendly browser-based User Interface for secure access from anywhere, for minimum ten concurrent connections from the Operator PC or other securely connected laptop/mobile, for plant monitoring, O&M, daily reporting, and analysis | Bidder requests client to confirm the exact requirement of Quantity (Nos) of 1. Browser (i.e. Laptop) based user access and 2. Mobile user licenses Kindly confirm. | Technical - Electrical | Bidder may consider as following: 1. Browser based user access - 20 Nos. 2. Mobile User licenses - 20 Nos. Please refer to Sl. No.34 of Amendment 01
307 | Technical Specification-Section VII | 260 | 2.1.4.1 | Before the commencement of PG test, the plant shall have completed Pre-PG tests as per Clause 2.1.1 above and SCADA system and WMS shall be fully commissioned and functional. | Bidder understands that one datalogger is sufficient for conducting the PG Test of both SCADA & WMS | Technical - Electrical | It is clarified that SCADA system and WMS shall be fully commissioned and functional such that data is available from SCADA system for assessment of OTGT Results.
308 | Technical Specification-Section VII | 66 | 14.3 | The Plant SCADA and Monitoring System may use one or more IIoT Controllers at each Inverter Control Room and MCR for the purpose of data acquisition and data forwarding to the SCADA Servers. | Bidder requests to accept the option of having PLC processor based architecture for SCADA design. Bidder wants to inform that, PLC processor based architecture is commonly used in Solar projects. Kindly provide your acceptance for the same. | Technical - Electrical | SCADA Architecture shall be IIoT based, as per specifications. Terms and conditions of the tender document shall prevail.
309 | Technical Specification-Section VII | 66 | 14.2.7 | Operator Workstation/PC shall be of Industrial Grade for browser-based access to plant data from Plant. Plant control & SLDC/Utility related operations shall only be initiated through browser-based interface requiring no client software or database to be installed on the Workstation | Bidder wishes to clarify that, As the SCADA OEM's (Vendors) works on independent methodology as per their System design, Browser based interface / Server-Client based design / any other applicable as per technical needs, shall be finalized during detailed engineering based on SCADA vendor recommendation to meet the SCADA specifications. Kindly provide your acceptance for the same | Technical - Electrical | The terms and conditions of the tender document shall prevail.
310 | Technical Specification-Section VII | 65 | 14.2.5 | Plant SCADA Server shall have Industrial Grade server hardware running SCADA & Monitoring Software with data storage (complete plant data) space for 2 years. | Bidder wishes to clarify that, As the SCADA OEM's (Vendors) works on independent methodology as per their System design, Browser based interface / Server-Client based design / any other applicable as per technical needs, shall be finalized during detailed engineering based on SCADA vendor recommendation to meet the SCADA specifications. Kindly provide your acceptance for the same | Technical - Electrical | The terms and conditions of the tender document shall prevail.
311 | Technical Specification-Section VII | 69 | 14.7.1 | All RS485, IO and CAT6 cables shall be laid in separate conduits with a minimum separation of 1.5ft from AC/DC power cables all along. | a. Bidder wishes to clarify that as RS 485 and IO cables are armoured cables, Conduits are not required. Hence we propose not to consider conduits for armoured communication and IO cables. b. As per IS 1255 standard, it is specified that, 300 mm (1 foot) clearance can be provided between Power and Communication cables, and hence the same can be followed for all communication & Instrumentation IO cables. Kindly provide your acceptance for the same. | Technical - Electrical | The terms and conditions of the tender document shall prevail.
312 | Technical Specification-Section VII |  | 14.7.2 | Power cables shall be laid deep in the trenches first. Data cables shall be laid in separate conduits after partially filling the trenches to ensure minimum 1.5 ft separation between power and communication cables all along the trench |  | Technical - Electrical | The terms and conditions of the tender document shall prevail.
313 | Technical Specification-Section VII |  | 14.7.3 | IO Cables between switch gear panels and SCADA panel shall be laid on separate cable trays, with a minimum of 1.5ft separation from trays carrying AC Power cables. |  | Technical - Electrical | The terms and conditions of the tender document shall prevail.
314 | Technical Specification-Section VII |  | 14.7.4 | RS485 & CAT6 cables between switch gear panels or Inverters and SCADA panel shall be laid on separate cable trays, with a minimum of 1.5ft separation from trays carrying AC Power cables. |  | Technical - Electrical | The terms and conditions of the tender document shall prevail.
315 | Technical Specification-Section VII | 70 | 14.10.2 | Operating System and Database shall be of enterprise scale (RedHat Linux or equivalent Linux OS, Oracle/MySQL or Windows or equivalent DB), with required AMC for 5 years | Bidder proposes that, it is recommended to consider Windows Server Operating System for Plant server as Windows Operating system is compatible for all standard SCADA software's. As per the Operator Workstation specifications, it is mentioned to consider Windows operating system, hence for integration of Plant Server and Operator Workstation, Bidder recommends to consider Windows based operating system for both Plant server and Operator Workstation. Kindly provide your acceptance for the same. | Technical - Electrical | Windows Server OS for the Plant Server is acceptable, provided it is enterprise-grade, ensures SCADA compatibility, meets cybersecurity and licensing norms, and complies with all tender specifications. Please refer Sl. No 23 of Amedment-1.
316 | Technical Specification-Section VII | 70 | 14.10.3 | Accessories: Intelligent UPS (on line): Minimum 2 hour battery backup. | Bidder proposes to consider common UPS system with 2 hours backup for SCADA as most of the loads will be for SCADA. Hence dedicated UPS only SCADA is not required. Please confirm your acceptance. | Technical - Electrical | There shall be separate UPS for SCADA as per Clause No. 14.10.3 of SS-B:TS-Electrical. Terms and conditions of the tender document shall prevail.
317 | Technical Specification-Section VII | 277 | 2.14 | The Energy Management System (EMS)/ Power Plant Controller (PPC) and SCADA system shall be connected with the Plant and the Contractor shall make arrangements to provide monthly reports from the SCADA system. The Contractor shall arrange to connect the Plant to the SCADA system operating at the Site enabling the remote operation of the Plant by the Contractor and to provide access to information pertaining to the Plant to the Employer’s Representative at Site and SLDC/RLDC. The Employer may collect the data generated by the SCADA system in respect of the Plant from the Contractor. | Bidder understands that Battery Energy Storage System is not applicable for this project. Kindly confirm. | Technical - Electrical | Battery Energy Storage System is not applicable for this project. Please refer the Scope of Works
318 | SECTION – VII SUB-SECTION B TECHNICAL SPECIFICATIONS (TS) – ELECTRICAL SYSTEM | Page No. 72 of 316 | 16 Power Transformer | As specified in Section VII: Sub Section - A (Scope of Works), Power Transformer of 33/220 kV ONAN/ONAF with OCTC Power Transformer shall be provided in line with “Standard Technical Specifications of Transformer(s) for Solar Park pooling station” issued by Central Electricity Authority (CEA). The transformer shall be capable of being overloaded to 110% for four hours in a 24-hour cycle. | Bidder request to confirm Power transformer 33/220 kV ONAN/ONAF with OCTC or 33/220 kV ONAN / ONAF with OLTC | Technical - Electrical | Power transformer 33/220 kV ONAN/ONAF shall be with OLTC. Please refer to Sl.No.33 of Amendment 01
319 | SECTION – VII SUB-SECTION B TECHNICAL SPECIFICATIONS (TS) – ELECTRICAL SYSTEM | Page No. 72 of 316 | 17 Nitrogen Injection Fire Protection System | The protection system shall prevent transformer oil tank explosion and possible fire in case of internal faults. In the event of fire by external causes such as bushing fire, OLTC fire, fire from surrounding equipment etc., it shall act as a fast and effective fire extinguisher without any manual intervention. |  | Technical - Electrical | No query
320 | SECTION – VII SUB-SECTION B TECHNICAL SPECIFICATIONS (TS) – ELECTRICAL SYSTEM | Page No. 74 of 316 | 17.3.4 Fire Detector | Adequate number of fire detectors shall be fitted on top cover of the transformer and OLTC with brackets. Heat sensing temperature of the fire detectors shall be 141°C. |  | Technical - Electrical | No query
321 | SECTION – VII SUB-SECTION B TECHNICAL SPECIFICATIONS (TS) – ELECTRICAL SYSTEM | Page No. 106 of 316 | 25 Power Evacuation System | 25.1 The Contractor shall design and construct the power evacuation system to and with the designated interconnection point (as mentioned in Sub Section A: Scope of Works) via either overhead transmission line or underground cables at specified grid voltage with all necessary infrastructure such as protection switchgears and metering systems as per the requirement of the CTU. | Bidder request to provide the preliminary estimated route length of 220kV transmission line and UG cable if applicable | Technical - Electrical | The interconnection point is specified in the Scope of Works as the 400/220 kV substation at Badnawar, Dhar (coordinates: 23.0363°N, 75.2118°E). Transmission line Right of Way is in the scope of the Bidder. (The aerial distance from the plant location to the interconnection point is approximately 25 km.)
322 | SECTION – VII SUB-SECTION B TECHNICAL SPECIFICATIONS (TS) – ELECTRICAL SYSTEM | Page No. 12 of 316 | 4 Procurement & Supply | 33/220 kV Solar park Substation with required number of 33 kV outdoor bays (including provision of extension on each side of the bus bar in future), required no. of 33/220 kV transformers, 220 kV Bays including Substation Automation System. Busbars, Equipment of Line Bay and Bus Coupler Bay shall be suitable for evacuation of 200 MVA. | Bidder request to confirm no. of line bays to be consider & 33kV PSS switchgear equipment to be consider 33kV outdoor AIS equipment or outdoor 33kV HT panel. | Technical - Electrical | Bidder shall consider 1 No. of 220 kV Line Bay. The bidder may propose 33 kV Switchgear Panels or outdoor AIS. Please refer Clause 4.12 of Scope of Works.
323 | SECTION – VII SUB-SECTION B TECHNICAL SPECIFICATIONS (TS) – ELECTRICAL SYSTEM | Page No. 12 of 316 | 4 Procurement & Supply | 220 kV bay at interconnecting substation (suitable for evacuation of 200 MVA) as per CTU drawings/specifications including shifting or replacement of substation equipment / materials, permits and approvals, CTU supervision and maintenance charges. | Bidder request to confirm interconnecting substation details like (1). 220 kV bay at interconnecting substation details like SLD, layout, Line & busbar schemes, system parameters & allocated bay details (2) Any extension of busbar, cable trench, roads etc. (3) Aux power supply details and availability of spare feeder details etc. (4) Dismantling & erection, shifting or replacement of existing substation equipment / materials. | Technical - Electrical | 1. Interconnecting Substation- 1 No. 220KV feeder bay at 400/220KV S/s Badnawar (feeder bay shall be constructed by Contractor) 2. 220KV DCSS line from project site up to 400/220KV S/s Badnawar (Approximate aerial distance 25kms) 3.Contractor will not be allowed to draw any power from the MP Grid except the start-up power for their project through the above interconnection. For the need of the power for other purpose / auxiliary power, contractor will have to take separate connection from DISCOM on behalf of SECI. 4. 220KV DCSS line and associated feeder bay shall be constructed by Contractor as per the requirement of MPPTCL
324 | SECTION – VII SUB-SECTION B TECHNICAL SPECIFICATIONS (TS) – ELECTRICAL SYSTEM | Page No. 13 of 316 | 4 Procurement & Supply | The Contractor shall provide provision to integrate Special Protection Scheme (SPS), if required, in case the RLDC requires the same. In that event, details of SPS and its setting shall be worked out in consultation with RLDC & RPC. | Bidders request to provide the telemetry protection system details at interconnecting substation and required equipment supply scope | Technical - Electrical | Will be provided subsequently.
325 | General |  |  |  | Bidder request to provide 33kV AC tender SLD & 33/220kV PSS tender SLD. | Technical - Electrical | Plant SLD is in the scope of bidder, to be finalised during detailed engineering.
326 | SECTION - VII SUB-SECTION A SCOPE OF WORKS | 6 / 316 | 1 Project Particulars | Cumulative Power Transformer Capacity : 250 MVA (2 X 125 MVA) Plant End Substation Power Transformer (33/220 kV) Capacity: 200 MVA (2 X 100 MVA) | Both the inputs are contradicting. Bidder request to clarify the power transformer capacity. | Technical - Electrical | Kindly refer to Sl.No. 17 of Amendment 1. Cumulative Power Transformer Capacity : 250 MVA (2 X 125 MVA) Plant End Substation Power Transformer (33/220 kV) Capacity: 250 MVA (2 X 125 MVA)
327 | Section - VII Sub Section C |  |  | General | Kindly share the kmz file of the proposed project site with clear demarcation of the plant boundary, CMCS location, 33/220kv solar park switchyard location, Interconnecting substation location and major approach road to the site. | Technical - Civil | KMZ file is not available. Refer to Sl. No. 56 of Amendment-1. CAD file has been shared along with coordinates of the interconnecting substation. Other details shall be finalized during detailed engineering.
328 | Section - VII Sub Section C |  |  | General | Kindly share the preliminary AutoCAD file of topography survey report. | Technical - Civil | KMZ file is not available. Refer to Sl. No. 56 of Amendment-1. CAD file has been shared.
329 | Section - VII Sub Section C |  |  | General | Kindly share the preliminary Geotechnical investigation report, water quality test report and hydrology survey report. | Technical - Civil | Reports are not available; These shall be in the scope of the EPC Contractor.
330 | Section - VII Sub Section C | 17/316 | 6.11 | For modules to be provided by the Owner, the Contractor shall provide storage areas in multiple locations within the plant area to receive and store them till installation. | Kindly confirm whether the 450 sq.m. storage area is considered as permanent store room during operation and maintenance. | Technical - Civil | Cl 6.11 referred to in the query is intended for storage of PV Modules prior to their installation. Query not clear
331 | Section - VII Sub Section C | 17/316 | 6.1 | Construction of outdoor storage shed of area sufficient enough to store spares. |  | Technical - Civil | Query not clear
332 | Section - VII Sub Section C | 18/316 | 6.12 | Construction of covered storage area (minimum 450 m2) for storage of spare modules and other spares. |  | Technical - Civil | Query not clear
333 | Section - VII Sub Section C | 114/316 | 3.8 | However, minimum grade of concrete shall be as specified under Cl.Error! Reference source not found. | Kindly mention the relevant clause. | Technical - Civil | Refer to Sl. No. 8 of Amendment-1.
334 | Section - VII Sub Section C | 116/316 | 3.1 | All buildings and Plinth for Open installations (MCR, ICR etc.), Transformer yard, Switchyard and Sub-station area shall have levelled ground as detailed under Clause No. Error! Reference source not found.. |  | Technical - Civil | Refer to Sl. No. 9 of Amendment-1.
335 | Section - VII Sub Section C | 119/316 | 6.2 | The Approach road connecting nearest public road and the Main gate shall be of 4.0m wide carriage way with 0.5m wide shoulders on either side. | Bidder proposes width of approach road as 3.5m wide with 0.5m shoulders on both side. | Technical - Civil | The terms and conditions of the tender document shall prevail.
336 | Section - VII Sub Section C | 117/316 | 5.1 | Module mounting structure foundation/ Pile cap or any other pedestal shall be min. 200mm above FGL. | Bidder proposes pile cap of 150mm above FGL for MMS. | Technical - Civil | The terms and conditions of the tender document shall prevail.
337 | Section - VII Sub Section A | 18/316 | 6.13 | Construction of one security room at main gate and watch towers at every land parcel / one for every 200 acres of land parcel inside the boundary of the plant. | Bidder understands that the watch towers should be considered at every parcel of land or one for every 200 acres of land for the project site. Kindly confirm. | Technical - Civil | Watch towers are to be considered at the rate of one watch tower for every 200 acres of land. However, in cases where the land parcels are non-contiguous or geographically separated, at least one watch tower shall be provided in each distinct parcel of land, irrespective of its size, to ensure adequate site surveillance and security. Accordingly, the bidder is required to provision watch towers either at the rate of one per 200 acres or one per land parcel—whichever results in a greater number of watch towers.
338 | Section - VII Sub Section C | 126/316 | 11.3 | Min. depth of foundation for all buildings and plinth for open installations shall be 1.5 m below NGL. | The depth of foundations shall be taken as per the geotechnical investigation report. Kindly confirm. | Technical - Civil | The terms and conditions of the tender document shall prevail.
339 | Section - VII sub section A | 18/316 | 7.1 | Obtaining statutory approvals /clearances/ compliances on behalf of the Employer from various Government Departments | Bidder request that approval from government agencies is the owner's scope. | Technical - Civil | The terms and conditions of the tender document shall prevail.

## Amendment-1
Balance of System tender for setting up of grid connected 200 MW Ground mounted Solar PV plant at Dhar, Madhya Pradesh
Tender No : SECI/C&P/OP/11/017/2024-25
S. No. | Section | Page No. | Clause | Original Version | Amendment
1 | SECTION - VII SUB-SECTION C | 12 of 58 | 5.3 | It is envisaged that the MMS are installed on natural/ existing ground without any levelling or grading of the area. Contractor shall accordingly consider the effect of the existing ground slope on the design of MMS structure as specified elsewhere in the specifications. If any ground undulations at column locations are observed the same shall be filled up with PCC (1:3:6) up to surrounding ground level immediately after pile installation before start of erection of other MMS members. In case of pile, the PCC fill shall extend min. 500mm outside pile cap all around and remaining area may be filled up with local soil properly compacted. | It is envisaged that the MMS are installed on natural/ existing ground without any levelling or grading of the area. Contractor shall accordingly consider the effect of the existing ground slope on the design of MMS structure as specified elsewhere in the specifications. If any ground undulations at column locations are observed the same shall be filled up with PCC (1:3:6) up to surrounding ground level immediately after pile installation before start of erection of other MMS members. In case of pile, the PCC fill shall extend min. 100mm outside pile cap all around and remaining area may be filled up with local soil properly compacted.
2 | SECTION - VII SUB-SECTION C | 19 of 58 | 10.10.1 | Module Mounting Structure (MMS) (additional requirements): The bidder shall conduct wind tunnel studies for the design and analysis of complete MMS, and the following shall be ensured: 1. It must be done from an institute of repute having suitable wind tunnel facilities (IITs, SERC Chennai or equivalent level institute in India.) 2. If the studies done by any reputed international facility, the study results must be vetted by the wind domain expert at any of the IITs or SERC or equivalent level institute in India. 3. Wind tunnel studies shall be specific to the site topography as well as array layout and shall be conducted in BLT tunnel as per guidelines specified in IS:875 – part 3 and ASCE MOP 67. 4. The wind tunnel studies shall be conducted with appropriate scale (however, not less than 1:50) model in boundary layer tunnel. | Module Mounting Structure (MMS) (additional requirements): The bidder shall conduct wind tunnel studies for the evaluation of wind loads on PV modules to be adopted for the analysis and design of MMS, and the following shall be ensured: 1. It must be done from an institute of repute having suitable wind tunnel facilities (IITs, SERC Chennai or equivalent level institute in India. 2. If the study is done by any reputed international facility, the study results must be vetted by the wind domain expert at any of the IITs or SERC or equivalent level institute in India. 3. Design wind speed shall be as per the requirements specified under Clause 10: Design Loads. 4. The wind tunnel studies shall be conducted with appropriate scale (however, in general not less than 1:50) model.
3 | SECTION - VII SUB-SECTION C | 19 of 58 | 10.10.2 |  | WL on the Module canopy shall be based on the findings of Wind Tunnel studies. Load due to wind action on exposed face of respective MMS members shall be as per IS 875 Part-3. WL shall be considered as detailed below: (i) WLx (downward, Cp+), WLz (downward, Cp+): Load due to positive pressure on PV modules at design tilt angle for wind acting in both (±X, ±Z) directions. (ii) WLx (upward, Cp-), WLz (upward, Cp-): Load due to negative pressure on PV modules at design tilt angle for wind acting in both (±X, ±Z) directions. (iii) WLx (member load), WLz (member load): Load due to wind action on side (exposed) face of respective MMS members for wind acting in both (±X, ±Z) directions. • ±WLx (member load, transverse to MMS table): Load due to wind action on column, front and back bracing, longitudinal bracing, tie-member or any other members. • ±WLz (member load, along length of MMS table): Load due to wind action on column, rafter, front and back bracing, longitudinal bracing, tie-member or any other members.
4 | SECTION - VII SUB-SECTION C | 21 of 58 | 12.2.1 | In case the contractor proposes to provide bored cast-in-situ concrete pile; the type, dia. and length of pile shall be as per recommendations of Geotechnical investigation report corresponding to prevalent soil characteristics at site. However, the min. dia and depth of the pile shall be 300mm (Min 350 mm for column depth more than 175 mm) and 1500 mm respectively except when very hard strata/ rock (N>100) is encountered at a higher level, the pile shall be extended in to the hard strata minimum 1.5 times the diameter of the pile with total depth of the pile not less than 1200mm below cut-off level. A minimum clear cover of 50 mm shall be provided to the steel section or reinforcement in the pile. | In case the contractor proposes to provide bored cast-in-situ concrete pile; the type, dia. and length of pile shall be as per recommendations of Geotechnical investigation report corresponding to prevalent soil characteristics at site. However, the min. dia and depth of the pile shall be 300mm and 1500 mm respectively except when very hard strata/ rock (N>100) is encountered at a higher level, the pile shall be extended in to the hard strata minimum 1.5 times the diameter of the pile with total depth of the pile not less than 1200mm below cut-off level. A minimum clear cover of 50 mm shall be provided to the steel section or reinforcement in the pile.
5 | SECTION - VII SUB-SECTION C | 25 of 58 | 13.7 |  | MAGNELIS
6 | SECTION - VII SUB-SECTION C | 27 of 58 | 13.14 | The vertical diagonal bracing shall be provided in end spans and every alternate span for all rows of columns of each unit (table) of MMS. The bracing arrangement shall be centre line symmetric | The vertical diagonal bracing shall be provided in end span for all rows of columns of each unit (table) of MMS. The bracing arrangement shall be centre line symmetric.
7 | SECTION - VII SUB-SECTION C | 28 of 58 | 13.23 | Fasteners and washers to be used for erection of mounting structure and for fixing the module shall be of stainless steel grade SS 304, with property class A2-70 conforming to relevant ISO standard and must sustain the adverse climatic conditions to ensure the life of the structure for 25 years. | Fasteners and washers to be used for fixing the module shall be of stainless-steel grade SS 304, with property class A2-70 conforming to relevant ISO standard. Fasteners and washers to be used for the erection of module mounting structure shall be HDG and of grade 8.8 conforming to IS 1367 and must sustain the adverse climatic conditions to ensure the life of the structure for 25 years.
8 | SECTION - VII SUB-SECTION C | 8 of 58 | 3.8 | The report shall also include ground water analysis (water sample collected from bore well) to ascertain its suitability for construction purposes, recommendations for type of cement, grade of concrete & minimum cement content as per prevalent soil characteristics with respect to presence of aggressive chemicals and environment exposure conditions as per relevant BIS specifications. However, minimum grade of concrete shall be as specified under Cl.Error! Reference source not found. ‘Concrete Works’ | The report shall also include ground water analysis (water sample collected from bore well) to ascertain its suitability for construction purposes, recommendations for type of cement, grade of concrete & minimum cement content as per prevalent soil characteristics with respect to presence of aggressive chemicals and environment exposure conditions as per relevant BIS specifications. However, minimum grade of concrete shall be as specified under Cl.14 ‘Concrete Works’.
9 | SECTION - VII SUB-SECTION C | 10 of 58 | 3.1 | All buildings and Plinth for Open installations (MCR, ICR etc.), Transformer yard, Switchyard and Sub-station area shall have levelled ground as detailed under Clause No. Error! Reference source not found. | All buildings and Plinth for Open installations (MCR, ICR etc.), Transformer yard, Switchyard and Sub-station area shall have levelled ground as detailed under Clause No. 5.
10 | SECTION - VII SUB-SECTION C | 16 of 58 | 7.1 | In case of rectangular drain, the thickness of the wall shall be checked against structural stability under action of the design loads as specified in Cl. No. Error! Reference source not found. ‘Design Loads’. However, the min. wall thickness shall be 230mm, 300mm and 125mm respectively for brick masonry, RR masonry and RCC work, except for garland drain around buildings where the min. wall thickness can be 115mm, 200mm and 100mm respectively for brick masonry, RR masonry and RCC work. | In case of rectangular drain, the thickness of the wall shall be checked against structural stability under action of the design loads as specified in Cl. No. 10 ‘Design Loads’. However, the min. wall thickness shall be 230mm, 300mm and 125mm respectively for brick masonry, RR masonry and RCC work, except for garland drain around buildings where the min. wall thickness can be 115mm, 200mm and 100mm respectively for brick masonry, RR masonry and RCC work.
11 | SECTION - VII SUB-SECTION C | 25 of 58 | 12.5 | Unless specified else were, the field trials for initial load tests on concrete and helical/ screw pile shall conform to IS: 2911 (Part 4) & Practice Note-28 (IPENZ Engineers New Zealand) as applicable. The no. and location of such tests shall be as per the provisions stipulated under Cl. No. Error! Reference source not found. | Unless specified else were, the field trials for initial load tests on concrete and helical/ screw pile shall conform to IS: 2911 (Part 4) & Practice Note-28 (IPENZ Engineers New Zealand) as applicable. The no. and location of such tests shall be as per the provisions stipulated under Cl. No. 3.9.3.
12 | SECTION - VII SUB-SECTION C | 26 of 58 | 13.8 | The primary loads and load combinations for design of MMS structure shall be as specified under Clause No. Error! Reference source not found. The design shall be done by Working stress method and no increase in allowable stress shall be permitted. | The primary loads and load combinations for design of MMS structure shall be as specified under Clause No. 10. The design shall be done by Working stress method and no increase in allowable stress shall be permitted.
13 | SECTION - VII SUB-SECTION C | 25 of 58 | 13.6 | The MMS stub/ column, rafter, purlin, ties and bracing members shall conform to following Indian standards. • IS: 2062 – Hot rolled Medium and High tensile structural steel • IS: 811 – Cold formed light gauge structural steel sections • IS: 1161 – Steel tubes for structural purposes • IS: 4923 – Hollow steel sections for structural use | The MMS stub/ column, rafter, purlin, ties and bracing members shall conform to following Indian standards: • IS: 2062 – Hot rolled Medium and High tensile structural steel • IS: 811 – Cold formed light gauge structural steel sections • IS: 1161 – Steel tubes for structural purposes • IS: 4923 – Hollow steel sections for structural use • IS 15961 - Hot-dip Aluminium-Zinc alloy metallic coated steel strip and sheet • IS 18513 - Hot-Dip Zinc-Aluminium-Magnesium Alloy Coated Steel Sheets, Plates and Strips
14 | SS-B:TS-Electrical | 18 of 82 | 5.3.3 | The panel enclosure shall be constructed with CRCA steel/Aluzinc sheet. The thickness of load bearing members shall be minimum 3 mm and that of non-load bearing members shall be minimum 2 mm. | Switchgear Panel material & thickness shall be as per OEM type tested design.
15 | SECTION VII | TOC- SS-E |  | - | SA-B : Project Specific Technical Details
16 | SECTION - VII SUB-SECTION E | SA-B |  | - | SA-B : Project Specific Technical Details. (Amended Document attached herewith)
17 | SS-A: SOW | 3 of 21 | 1 | Plant End Substation Power Transformer (33/220 kV) Capacity: 200 MVA (2 X 100 MVA) | Plant End Substation Power Transformer (33/220 kV) Capacity: 250 MVA (2 X 125 MVA)
18 | SS-A: SOW | 3 of 21 | 1 | DC Capacity: 260 MWp | DC Capacity: 260 MWp (Note: Actual DC capacity which shall be provided by Employer may vary in the range of +/- 10%, consequent variation in contract price shall be calculated as per Contract Price Variation Clause of this Tender Document mentioned elsewhere)
19 | SS - F: O&M Agreement | 36 of 43 | 1 | ANNEXURE-2: 1. Annual PR Guarantee | ANNEXURE-2: 1. Annual Generation Guarantee
20 | SS - F: O&M Agreement | 36 of 43 | 1. B. | ANNEXURE-2: 1. B. The Contractor guarantees of Plant Performance Ratio over the year committed herein over the O&M Period (“Annual PR Guarantee”) from the date of Operational Acceptance. In the event the PR is less than the Guaranteed PR, the Contractor shall immediately, upon demand, indemnify the Employer, as liquidated damages and not as penalty, amounts equivalent to estimated energy loss, subject to a maximum of seventy (70%) percent of the Total Annual O&M Contract Value. | ANNEXURE-2: 1. B. The Contractor shall guarantee the Target Generation (post-OTGT) for each year during the O&M Period (“Annual Generation Guarantee”), from the date of Operational Acceptance. In the event that the Actual Generation is less than the Guaranteed Target Generation (GTN), the Contractor shall, upon demand, indemnify the Employer by paying liquidated damages - not as a penalty - equivalent to the estimated energy loss. This indemnity shall be subject to a maximum of five percent (5%) of the revenue from the Target Generation (GTN), calculated at the ceiling tariff specified below. • Ceiling tariff - Rs. 2.57 per unit
21 | SS - F: O&M Agreement | 36 of 43 | 1. C. | ANNEXURE-2: 1. C. Performance Ratio (PR) for Solar Plant shall be calculated as per the detailed procedure provided in General Annexure-J: FG Test Procedure. Towards the demonstration of Functional Guarantees under this O&M Agreement, the Annual PR shall be calculated as the mean of PR calculated on a monthly basis (over the total no. of days in the month) as per the procedure specified under Clause 2.1.4.2 therein (i.e. FG Test Procedure) Annual PR = mean of monthly PR
22 | SS - F: O&M Agreement | 36 of 43 | 1. D. | ANNEXURE-2: 1. D. Liquidated Damages for Shortfall in Annual PR for Solar PV Plant If the Contractor fails to achieve annual guaranteed PR at the end of an Year, but PR achieved is not less than 5% from the guaranteed PR (eg, if guaranteed PR is 81%, and 76% >= PR achieved <= 81%), the Contractor shall be liable for liquidated damages to the Employer (amount to be deducted from the payment due towards O&M of the Plant under the Contract, as per below: Liquidated Damages (LD) = (PRg – PRa)/0.05 x 0.7 x Annual O&M Contract Value Where, PRg = Annual PR Guarantee as per O&M Contract PRa = Actual PR achieved Note: (i) For the purpose of above calculation numerical value of the PR shall be considered with up to 3 significant decimal places. Eg. 0.811. (ii) The Invoices raised by the O&M Contractor during the year (when Annual PR has not been calculated), shall be paid by the Employer after deducting LD, if applicable, as per above formula, on the basis of average PR for the invoice period. (iii) In case Annual PR guarantee is demonstrated by the O&M Contractor, any amount deducted as LD towards shortfall in PR during the year shall be reversed.
23 | SS-B:TS-Electrical | 46 of 82 | 14.10.2 | Operating System and Database shall be of enterprise scale (OS - RedHat Linux or Windows Server or equivalent Linux OS; DB - Oracle/MySQL or Windows or equivalent DB), with required AMC for 5 years. | Operating System (OS) and Database (DB) shall be of enterprise scale (OS - RedHat Linux/equivalent Linux/Widows Server OS; Database - Oracle/MySQL/equivalent DB), with required AMC for 5 years
24 | SS-A: SOW | 4 of 21 | 1
25 | GA-J | 256 of 316 | GA-J | GENERAL ANNEXURE J: Functional Guarantee (FG) Test Procedure (Existing) | GENERAL ANNEXURE J: Functional Guarantee (FG) Test (OTGT) Procedure (Amended Document attached herewith)
26 | SS-A: SOW | 4 of 21 | 1
27 | SS-A: SOW | 10 of 21 | 4.32 | 4.32 Weather monitoring station shall include but not be limited to the following: • Pyranometers – Two in Horizontal Plane for GHI and two in inclined plane – Minimum 4 (Four) Nos. • Ultrasonic Anemometer (wind speed and direction) – 1 (one) no. • Temperature Sensor (ambient and module surface) – 5 (five) nos. • Sensors required for measurement of following parameters (i) Rainfall (mm) (ii) Relative humidity (%) • Power source to the all sensors wherever required • Data Logger | 4.32 Weather monitoring station shall include but not be limited to the following and shall be spatially distributed throughout the plant area: • Pyranometers – 4 (four) nos. in Horizontal Plane for GHI and 4 (four) nos. in inclined plane • Ultrasonic Anemometer (wind speed and direction) – 4 (four) nos. • Temperature Sensor with shielding case (ambient) – 4 (four) nos. • Temperature Sensor (module surface) – 12 (twelve) nos. • Sensors required for measurement of following parameters (i) Rainfall (mm) 4 (four) nos. (ii) Relative humidity (%) 1(one) nos. • Power source to the all sensors wherever required • Data Logger
28 | SS-B:TS-Electrical | 76 of 82 | 21.1.4 | A total of 10 pyranometers (5 for GHI measurement, 5 for GTI measurement) shall be provided and shall be spatially distributed throughout the plant area, as is possible. | VOID
29 | SS-B:TS-Electrical | 76 of 82 | 21.2.2 | The Contractor shall provide minimum 5 (five) temperature sensors for ambient temperature measurement with shielding case and 30 (thirty) for module temperature measurement. Sensors should be spatially distributed throughout the plant area, as is possible | VOID
30 | SS-B:TS-Electrical | 76 of 82 | 21.4 | 21.4 Sensors required for measurement of following parameters shall also be provided. (i) Rainfall (mm) – 5 nos. (ii) Relative humidity (%) – 5 nos. | VOID
31 | SECTION - VII SUB-SECTION E | SA-A |  | Tentative Land Layout with Contour Details | Amended CAD file (SA - A_Tentative Land Layout with Contour Details) is attached with Amendment 01.
32 | SS-A: SOW | 4 of 21 | 1 | - | Metering Point: 220 kV side of Interconnecting 400/220kV Substation Badnawar
33 | SS-B:TS-Electrical | 48 of 82 | 16 | As specified in Section VII: Sub Section - A (Scope of Works), Power Transformer of 33/220 kV ONAN/ONAF with OCTC Power Transformer shall be provided in line with “Standard Technical Specifications of Transformer(s) for Solar Park pooling station” issued by Central Electricity Authority (CEA). The transformer shall be capable of being overloaded to 110% for four hours in a 24-hour cycle. | As specified in Section VII: Sub Section - A (Scope of Works), Power Transformer of 33/220 kV ONAN/ONAF with OLTC Power Transformer shall be provided in line with “Standard Technical Specifications of Transformer(s) for Solar Park pooling station” issued by Central Electricity Authority (CEA). The transformer shall be capable of being overloaded to 110% for four hours in a 24-hour cycle.
34 | SS-B:TS-Electrical | 44 of 82 | 14.5.6 | The SCADA system shall have user-friendly browser-based User Interface for secure access from anywhere, for minimum ten concurrent connections from the Operator PC or other securely connected laptop/mobile, for plant monitoring, O&M, daily reporting, and analysis. | The SCADA system shall have a user-friendly, browser-based user interface for secure access from anywhere, supporting 20 browser-based user accesses and 20 mobile user licenses, for plant monitoring, O&M, daily reporting, and analysis
35 | SS-B:TS-Electrical | 14 of 82 | 4.3.18 | Fire-protection for inverter transformer shall be provided in accordance with relevant CEA regulations as amended time to time | Fire-protection for inverter transformer shall be provided in accordance with relevant CEA regulations as amended time to time. (Note: Automatic Fire Protection System (including NIFPS) to be provided for transformers above 10 MVA, as per CEA (Measures Relating to the Safety and Electric Supply), Regulations 2023.)
36 | Section V Special Conditions of Contract | 2 of 12 | 3 | The Time for Commissioning for the cumulative capacity of 200 MW Ground mounted Solar PV Power Plant at Dhar along with other associated equipment as per this tender document in total shall be 12 (Twelve) Months from the Date of the signing of Contract Agreement. | The Time for Commissioning for the cumulative capacity of 200 MW Ground mounted Solar PV Power Plant at Dhar along with other associated equipment as per this tender document in total shall be 15 (Fifteen) Months from the Date of the signing of Contract Agreement.
37 | Section V Special Conditions of Contract | 2 of 12 | 3.2 | Date of successful commissioning - D+12 months | Date of successful commissioning - D+15 months
38 | Section V Special Conditions of Contract | 5 of 12 | 9 | First Stage (Supply and Services): The value of the Contract Performance Security shall be 5% (Five percent) of the Contract Value (i.e., total sum of the Supply & Service Contract). This Performance security will be valid for a total period of 75 Months (12 Months Project commissioning period) + prescribed O & M Period, i.e., 60 Months + 03 Months additional) from the date of its issuance. The successful bidder can submit Contract Performance Security with initial validity of 36 months and the same may be extended after every 36 months till completion of the total 75 months period. ....... 5. Payment on Order Instrument (POI) against PBG: As an alternative to submission of PBG as above, the successful bidder also has an option to submit a letter of undertaking issued by either of the following three organizations, viz. (i) Indian Renewable Development Agency Limited (IREDA) or (ii) Power Finance Corporation Limited or (iii) REC Limited. | First Stage (Supply and Services): The value of the Contract Performance Security shall be 5% (Five percent) of the Contract Value (i.e., total sum of the Supply & Service Contract). This Performance security will be valid for a total period of 78 Months (15 Months Project commissioning period) + prescribed O & M Period, i.e., 60 Months + 03 Months additional) from the date of its issuance. The successful bidder can submit Contract Performance Security with initial validity of 36 months and the same may be extended after every 36 months till completion of the total 78 months period. ....... 5. Payment on Order Instrument (POI) against PBG: As an alternative to submission of PBG as above, the successful bidder also has an option to submit a letter of undertaking issued by either of the following three organizations, viz. (i) Power Finance Corporation Limited or (ii) REC Limited.
39 | Annexure to Bid Data Sheet (BDS) Qualifying Requirements | 6 of 11 | 1.3 | The bidder should have a minimum Working Capital of INR 94,00,00,000/- (Indian Rupees Ninety-Four crores only) as per the last audited financial statement. If the bidder’s working capital is inadequate, the bidder should supplement this with a letter from the bidder’s bank, having net worth not less than INR 500 Crores, confirming availability of the line of credit for more than or equal to INR 94,00,00,000/- (Indian Rupees Ninety-Four crores only) to meet the working Capital requirement of this particular Project. | The bidder should have a minimum Working Capital of INR 75,00,00,000/- (Indian Rupees Seventy-Five crores only) as per the last audited financial statement. If the bidder’s working capital is inadequate, the bidder should supplement this with a letter from the bidder’s bank, having net worth not less than INR 500 Crores, confirming availability of the line of credit for more than or equal to INR 75,00,00,000/- (Indian Rupees Seventy-Five crores only) to meet the working Capital requirement of this particular Project.
40 | Section IV General Conditions of Contract | 23 of 82 | 20.1 | Subject to Force Majeure Clause, if the Contractor fails to comply with the Time for Completion /successful commissioning or any extension thereof of Plant facilities in accordance with timelines as mentioned under the SCC, then the Contractor shall pay to the Owner a sum equivalent to half percent (0.5%) per week of the Contract Price for the whole of the facilities as liquidated damages for such default and not as a penalty, without prejudice to the Owner’s other remedies under the Contract subject to the maximum limit of five percent (05%) of Contract Price for the whole of the facilities. The Owner may, without prejudice to any other method of recovery, deduct the amount of such damages from any amount due or to become due to the Contractor. The payment or deduction of such damages shall not relieve the Contractor from his obligation to complete the Works, or from any other of his obligations and liabilities under the Contract. Owner may consider the termination of contract and/or shall have the discretion of getting executed the work from the Contractor once the maximum limit of LD is reached. Any such recovery on account of the Liquidated damages can be done from the running bills of the Contractor by Owner. | Subject to Force Majeure Clause, if the Contractor fails to comply with the Time for Completion /successful commissioning or any extension thereof of Plant facilities in accordance with timelines as mentioned under the SCC, then the Contractor shall pay to the Owner a sum equivalent to half percent (0.5%) per week of the uncommission part of the facilities as liquidated damages for such default and not as a penalty, without prejudice to the Owner’s other remedies under the Contract subject to the maximum limit of five percent (05%) of Contract Price for the whole of the facilities. The Owner may, without prejudice to any other method of recovery, deduct the amount of such damages from any amount due or to become due to the Contractor. The payment or deduction of such damages shall not relieve the Contractor from his obligation to complete the Works, or from any other of his obligations and liabilities under the Contract. Owner may consider the termination of contract and/or shall have the discretion of getting executed the work from the Contractor once the maximum limit of LD is reached. Any such recovery on account of the Liquidated damages can be done from the running bills of the Contractor by Owner.
41 | Section V Special Conditions of Contract | 8 of 12 | 15 (A) | All payment shall be made against invoices raised in line with the approved billing. All payment shall be made against invoices raised ……. A. The payment for the Supply Portion of the First Contract (Supply Contract) shall be made as per the following terms and conditions: ...... (iv) Final Ten percent (10%) payment of Supplies shall be paid against submission of the BG of the equivalent amount & against the Operational Acceptance of the plant Facility pursuant to successful Guarantee Tests and demonstration of Performance Ratio (PR) including submission of all as-built drawings and O&M manual. This BG shall be valid for a period of 18 (Eighteen) months from the date of its issuance & will be released after CUF demonstration on completion of first year of O&M, pursuant to the submission of all requisite documentation up to the final acceptance of the Plant facilities. However, in case of any delay, the BG shall be extended suitably. | All payment shall be made against invoices raised in line with the approved billing. All payment shall be made against invoices raised ……. A. The payment for the Supply Portion of the First Contract (Supply Contract) shall be made as per the following terms and conditions: ...... (iv) Final Ten percent (10%) payment of Supplies shall be paid against submission of the BG of the equivalent amount & against the Operational Acceptance of the plant Facility pursuant to successful O&M Target Generation Test including submission of all as-built drawings and O&M manual. This BG shall be valid for a period of 18 (Eighteen) months from the date of its issuance & will be released after target generation demonstration on completion of first year of O&M, pursuant to the submission of all requisite documentation up to the final acceptance of the Plant facilities. However, in case of any delay, the BG shall be extended suitably.
42 | Section V Special Conditions of Contract | 10 of 12 | 15 (B) | ii) For Erection, Testing and Commissioning Portion, the payment shall be made as detailed below: - …….. c) Final Ten percent (10%) payment of Services shall be paid against submission of the BG of the equivalent amount & against the Operational Acceptance of the plant Facility pursuant to successful Guarantee Tests and demonstration of Performance Ratio (PR) including submission of all as-built drawings and O&M manual. This BG shall be valid for a period of 18 (Eighteen) months from the date of its issuance & will be released after CUF demonstration on completion of first year of O&M, pursuant to the submission of all requisite documentation up to the final acceptance of the Plant facilities. However, in case of any delay, the BG shall be extended suitably. | ii) For Erection, Testing and Commissioning Portion, the payment shall be made as detailed below: - …….. c) Final Ten percent (10%) payment of Services shall be paid against submission of the BG of the equivalent amount & against the Operational Acceptance of the plant Facility pursuant to successful O&M Target Generation Test including submission of all as-built drawings and O&M manual. This BG shall be valid for a period of 18 (Eighteen) months from the date of its issuance & will be released after target generation demonstration on completion of first year of O&M, pursuant to the submission of all requisite documentation up to the final acceptance of the Plant facilities. However, in case of any delay, the BG shall be extended suitably.
43 | Section V Special Conditions of Contract | 11 of 12 | 15 (B) | iii) For Civil & Allied works portion, of the First contract, the payment shall be made as detailed below: …….. (c) Final Ten percent (10%) payment of Civil Works shall be paid against submission of the BG of the equivalent amount & against the Operational Acceptance of the plant Facility pursuant to successful Guarantee Tests and demonstration of Performance Ratio (PR) including submission of all as-built drawings and O&M manual. This BG shall be valid for a period of 18 (Eighteen) months from the date of its issuance & will be released after CUF demonstration on completion of first year of O&M, pursuant to the submission of all requisite documentation up to the final acceptance of the Plant facilities. However, in case of any delay, the BG shall be extended suitably. | iii) For Civil & Allied works portion, of the First contract, the payment shall be made as detailed below: …….. (c) Final Ten percent (10%) payment of Civil Works shall be paid against submission of the BG of the equivalent amount & against the Operational Acceptance of the plant Facility pursuant to successful O&M Target Generation Test including submission of all as-built drawings and O&M manual. This BG shall be valid for a period of 18 (Eighteen) months from the date of its issuance & will be released after target generation demonstration on completion of first year of O&M, pursuant to the submission of all requisite documentation up to the final acceptance of the Plant facilities. However, in case of any delay, the BG shall be extended suitably.
44 | Section IV General Conditions of Contract | 41 of 82 | 45 | 45. Operation & Maintenance 45.3 Breakdown / Corrective maintenance: Whenever a fault occurs, the Contractor has to attend to rectify the fault & the fault must be rectified within the 72 hours from the time of occurrence of fault. The Contractor must maintain all the records pertaining to all such faults and necessary measures taken. The date of Comprehensive Operation & Maintenance Contract period shall begin from the date of Operational acceptance. However, operation of the Power Plant means operation of system as per TS and workmanship in order to keep the project trouble free covering the O&M period. The Contractor must demonstrate the committed CUF at the end of every year in accordance with commitment made in line with the Performance guarantees. | 45. Operation & Maintenance 45.3 Breakdown / Corrective maintenance: Whenever a fault occurs, the Contractor has to attend to rectify the fault & the fault must be rectified within the 72 hours from the time of occurrence of fault. The Contractor must maintain all the records pertaining to all such faults and necessary measures taken. The date of Comprehensive Operation & Maintenance Contract period shall begin from the date of Operational acceptance. However, operation of the Power Plant means operation of system as per TS and workmanship in order to keep the project trouble free covering the O&M period. The Contractor must demonstrate the committed target generation at the end of every year in accordance with commitment made in line with the Performance guarantees.
45 | General | - | - | General Clarification regarding maintenance of plant during the interim period between Commissioning and Operational Acceptance | Operational Acceptance of the Plant Facilities by the Employer shall be a necessary condition for signing of the O&M Agreement. The Contractor shall, however, maintain the plant facilities, in the interim period between the Plant Commissioning and the signing of the O&M Agreement
46 | Section V Special Conditions of Contract | 7 of 12 | 12 | Conditions for Issue of Materials i) PV modules will be supplied to the Contractor by the Owner from the manufacturing plant. The transportation and unloading of the PV modules will be done by the supplier of the PV modules from the manufacturing plant to the designated storage location at the site. It shall be responsibility of the Contractor to take delivery of the materials and arrange for its storage at the Site of Work at his own cost. Once the material is issued or taken over by the Contractor, then the same will be his own liability to store, use & maintain. | Conditions for Issue of Materials i) PV modules will be supplied to the Contractor by the Owner from the manufacturing plant. The transportation of the PV modules will be done by the supplier of the PV modules from the manufacturing plant to the designated storage location at the site. It shall be responsibility of the Contractor to take delivery of the materials and arrange for its storage at the Site of Work at his own cost. Once the material is issued or taken over by the Contractor, then the same will be his own liability to store, use & maintain.
47 | Section V Special Conditions of Contract | 7 of 12 | 12 | Conditions for Issue of Materials v) It shall be duty of the Contractor to inspect the materials supplied to him at the time of taking delivery/handing over and satisfy himself that they are in good condition. After the materials have been delivered by the Owner, it shall be the responsibility of the Contractor to keep them in good condition and if the materials are damaged or lost, at any time, they shall be repaired and/ or replaced by him at his own cost. Upon identifying a damaged module post handing over of the Modules to the contractor, the contractor shall keep them in a separate storage and enlist them, upon verification, the entire damaged modules shall be replaced. In case of any discrepancy, the differential modules cost shall be debited from contractors' RA bills. | Conditions for Issue of Materials v) It shall be duty of the Contractor to inspect the materials supplied to him at the time of taking delivery/handing over and satisfy himself that they are in good condition. After the materials have been delivered by the Owner and inspected by supplier, BoS Contractor and SECI at site, it shall be the responsibility of the Contractor to keep them in good condition and if the materials are damaged or lost, at any time, they shall be repaired and/ or replaced by him at his own cost. Upon identifying a damaged module post handing over of the Modules to the contractor, the contractor shall keep them in a separate storage and enlist them, upon verification, the entire damaged modules shall be replaced. In case of any discrepancy, the differential modules cost shall be debited from contractors' RA bills. Further, in case the Module are inspected at later stage during the execution post the supply of Module by the supplier, the Contractor shall facilitate logistical requirement of the damage module to and fro from the site to the OEM facility.
49 | Section VI Sample Forms and Formats | - | Format-5 | PROFORMA OF "BANK GUARANTEE" FOR "PERFORMANCE BANK GUARANTEE (PBG)” | New Format attached with the Amendment 01.
50 | Section VI Sample Forms and Formats | - | Format-22 | List of Banks | VOID
51 | Section VI Sample Forms and Formats | - | Format-27 | FORMAT OF PAYMENT ON ORDER INSTRUMENT TO BE ISSUED BY REC/PFC (IN LIEU OF BG TOWARDS EMD) | New Format attached with the Amendment 01.
52 | Section VI Sample Forms and Formats | - | Format-28 | FORMAT OF PAYMENT ON ORDER INSTRUMENT TO BE ISSUED BY REC/PFC (IN LIEU OF BG TOWARDS PBG) | New Format attached with the Amendment 01.
53 | Section VI Sample Forms and Formats | - | Format-31 | Format for Surety Bond towards EMD | New Format attached with the Amendment 01.
54 | Section VI Sample Forms and Formats | - | Format-32 | Format for Surety Bond towards PBG | New Format attached with the Amendment 01.
55 | Section II Instructions to Bidders | 15 of 52 | 16 | 16.4 EMPLOYER/ Owner shall not be liable to pay any Bank charges, commission or interest etc. on the amount of 'EMD'. In case 'EMD' is in the form of a 'Bank Guarantee', the same shall be from any scheduled Bank as specified in the List of Banks enclosed at Form F-22, Section-VI of Tender documents or a branch of an International Bank situated in India and registered with 'Reserve Bank of India' as Scheduled Foreign Bank. However, in case of 'Bank Guarantee' from Banks other than the Nationalized Indian Banks, the Bank must be commercial bank having net worth in excess of INR 500 Crores (Indian Rupees Five Hundred Crores Only). | 16.4 The Bidder shall furnish the Bank Guarantees towards EMD issued by any Indian branch of a Scheduled Commercial Bank as listed on the website of Reserve Bank of India (RBI), as applicable on the date of issuance of bank guarantee
56 | SECTION - VII SUB-SECTION C | 43 of 58 | 34.2 | In case of transformer oil tank capacity ≥ 2000 litres, the transformer foundation shall have its own soak pit which would cover the area of the transformer and cooler banks, so as to collect any spillage of oil in case of emergency. The retention capacity of the soak pit shall be equal to volume of the transformer oil (excluding free space above gravel) and it shall be filled with granite stone gravel of size 40mm, uniformly graded, with 200 mm free space above gravel fill. | Requirement of Soak Pit and Oil collecting pit shall be as per CEA (Technical Standards for Construction of Electrical Plants and Electric Lines) Regulations.
57 | SECTION - VII SUB-SECTION C | 43 of 58 | 34.3 | In case of transformer oil tank capacity more ≥ 5000 litres, the soak pit shall be connected to a separate burnt oil pit through GI discharge pipe (300 mm dia) which shall be suitably sized to accommodate full oil volume (excluding free board above the bottom of inlet pipe) of the transformer connected to it. The inlet pipe shall be provided proper slope to avoid any backflow of the incoming oil. In this case the capacity of the soak pit of the transformer may be reduced max. up to 1/3rd of the total transformer oil volume. The burnt oil pit shall be further connected to oil separation/ treatment system. The water shall be discharged into the nearest drain by gravity flow or pumping after suitable treatment as per statutory and code provisions. | Requirement of Soak Pit and Oil collecting pit shall be as per CEA (Technical Standards for Construction of Electrical Plants and Electric Lines) Regulations.
58 | SECTION - VII SUB-SECTION A Scope of Works | 8 of 21 | 4.1 | It shall be the responsibility of the Owner to supply PV Modules at Project site, between 6 (six) to 11 (eleven) months from date of award of the Contract. | It shall be the responsibility of the Owner to supply PV Modules at Project site, between 5 (five) to 13 (thirteen) months from date of award of the Contract.
59 | Section II Instructions to Bidders | 29 of 52 | 32.4.2 7(c) | The Final Contract Price emerged post applying the above mentioned adjustments in the Contract Price post e-RA of the successful bidder will be the Contract Price on which the Contract will be awarded to the successful bidder. | The Final Contract Price emerged post applying the above mentioned adjustments in the Contract Price post e-RA of the successful bidder will be the Contract Price on which the Contract will be awarded to the successful bidder. Further, such adjustmenst will also be exercised in determining the final Contract Value to be paid to the Contractor, once the Module Supply is completed and final price adjustment factor is determined based on the actual supply of Modules Specifications. Such correction in the final Contract Value of the BoS Contract may so happen mid course once the complete Module supply is done or during the Final Closure of the project.